## WWTFs
Wastewater Treatment Plants | Treatment Operator | Facility Type | Design Capacity MGD | Wastewater Treatment Plants | Permit Number | LRP Certification | Effluent Sample Type | Copy of Certification | Latitude/Longitude | Wastewater Treatment Plants | Permit Number | Copy of Certification | 2015 BCWA Sample Collection & Reporting | Wastewater Treatment Plants | Permit Number | Facility Type | Design Capacity MGD
Bear Creek Drainage |  |  |  | Bear Creek Drainage | [5 empty] | Bear Creek Drainage |  |  |  | Bear Creek Drainage
JCS Outdoor Lab | JCS, Kim Brogan | Minor | 0.0075 | Singing River Ranch | CO-0035971 | Todd Amen | grab | Yes | 39.37' 26.43/ 105.26' 33.21 | JCS Outdoor Lab | CO-0032514 | Not Needed |  | Singing River Ranch | CO-0035971 | Minor | 0.014
Brookforest Inn | Treatment Tech | Minor | 0.009 | JCS Outdoor Lab | CO-0032514 | Kim Brogan | Groundwater | Not Needed | Not Sampled | Brookforest Inn | CO-0030261 | Yes |  | JCS Outdoor Lab | CO-0032514 | Minor | 0.0075
Evergreen Metro District | EDM | Minor | 0.99 | Brookforest Inn | CO-0030261 | Robert Clodfelter | grab | Yes | 39.579394/ 105.380764 | Evergreen Metro District | CO-0031429 | Yes | Yes | Brookforest Inn | CO-0030261 | Minor | 0.009
West Jefferson County Metro District | EDM | Minor | 0.7 | Evergreen Metro District | CO-0031429 | Dave Lighthart | Composite12-hour | Yes | 39.38' 16.19/105.18' 56.07 | West Jefferson County Metro District | CO-0020915 | Yes | Yes | Evergreen Metro District | CO-0031429 | Minor | 0.99
Kittredge Water and Sanitation District | EDM | Minor | 0.125 | Bear Creek Cabins | CO-0030856 | Robert Clodfelter | grab | Yes | 39.38' 43/ 105.18' 26 | Kittredge Water and Sanitation District | CO-0023841 | Yes | Yes | Bear Creek Cabins | CO-0030856 | Minor | 0.001
Genesee Water and Sanitation District | Genesee | Minor | 0.8 | West Jefferson County Metro District | CO-0020915 | Dave Lighthart | Composite12-hour | Yes | 39.39' 46.05/105.20' 06.62 | Genesee Water and Sanitation District | CO-0022951 | Yes | Yes | West Jefferson County Metro District | CO-0020915 | Minor | 0.7
Forest Hills Metro District | Bryan McCarty/ Will Raatz | Minor | 0.05 | Kittredge Water and Sanitation District | CO-0023841 | Dave Lighthart | Composite12-hour | Yes | 39.39' 27.75/105.17' 15.04 | Forest Hills Metro District | CO-0037044 | Yes | Yes | Kittredge Water and Sanitation District | CO-0023841 | Minor | 0.125
Morrison | Town of Morrison | Minor | 0.35 | Genesee Water and Sanitation District | CO-0022951 | Chris Brownell | Composite 24-hour | Yes | 39.40' 34/ 105.16' 26 | Morrison | CO-0041432 | Yes | Yes | Genesee Water and Sanitation District | CO-0022951 | Minor | 0.8
Turkey Creek Drainage |  |  |  | Forest Hills Metro District | CO-0037044 | Bruce McCreary | Composite12-hour | Yes | 39.42' 09/ 105.15' 07 | Turkey Creek Drainage |  |  |  | Forest Hills Metro District | CO-0037044 | Minor | 0.05
Aspen Park Metro District | Treatment Tech | Minor | 0.025 | Morrison | CO-0041432 | John McEncroe | Composite12-hour | Yes | 39.39' 10.89/ 10510' 39.99 | Aspen Park Metro District | CO-0631016 | Yes |  | Morrison | CO-0041432 | Minor | 0.35
Conifer Metro District | Bryan McCarty | Minor | 0.043 | Turkey Creek Drainage | [5 empty] | Conifer Metro District | CO-047295/ COG589060 | Not Needed |  | Turkey Creek Drainage
Conifer Sanitation Association | Becky Hammer, Wayne Ramey | Minor | 0.019 (Liftstation) | Aspen Park Metro District | CO-0631016 | Robert Clodfelter | Composite12-hour | Yes | 39.32' 38/ 105.17' 25 | Conifer Sanitation Association | COX-0047392 | Yes | Yes | Aspen Park Metro District | CO-0631016 | Minor | 0.025
JCS Conifer High School | JCS, Kim Brogan | Minor | 0.052 | Conifer Metro District | CO-047295 | Bryan McCarty | Groundwater | Yes | Not Sampled | JCS Conifer High School | CO-047988 | Yes | Yes | Conifer Metro District | CO-047295/ COG589060 | Minor | 0.043
Tiny Town | Treatment Tech | Minor | 0.005 | Conifer Sanitation Association | COX-0047392 | Becky Hammer | Grab | Yes | 39.31' 49/ 105.18' 16 | Tiny Town | CO-0036129 | Yes |  | Conifer Sanitation Association | COX-0047392 | Minor | 0.019 (Liftstation)
Geneva Glen | Crystal Clear Water Treatment/ Russ Brown | Minor | 0.0105 | JCS Conifer High School | CO-047988 | Kim Brogan | Composite12-hour | Yes | 95.523470/ 105.306350 | Geneva Glen | CO-0044652 | Not Needed |  | JCS Conifer High School | CO-047988 | Minor | 0.052
The Fort | Treatment Tech | Minor | 0.012 | Tiny Town | CO-0036129 | Robert Clodfelter | grab | Yes | 39.36' 22/105.13' 38 | The Fort Resturant | NA | Not Needed |  | Tiny Town | CO-0036129 | Minor | 0.005
|  |  |  | Geneva Glen | CO-0044652 | Ken Atchison | Groundwater | Not Needed | Not Sampled |  |  |  |  | Geneva Glen | CO-0044652 | Minor | 0.0105
|  |  |  | The Fort Resturant | NA | Robert Clodfelter | Groundwater | Not Needed | Not Sampled |  |  |  |  | The Fort | NA | Minor | 0.012
[14 empty] | Evergreen Metro District | CO-0031429
[14 empty] | West Jefferson County Metro District | CO-0020915
[14 empty] | Kittredge Water and Sanitation District | CO-0023841
[14 empty] | Genesee Water and Sanitation District | CO-0022951
[14 empty] | Forest Hills Metro District | CO-0037044
Conifer Metro District
[14 empty] | Conifer Sanitation Association | COX-0047392
[14 empty] | JCS Conifer High School | CO-047988
[14 empty] | JCS Outdoor Lab | CO-0032514
[14 empty] | Morrison | CO-0041432

## Load
Load (pounds) = discharge(MG)* Concentration* 8.34 |  |  |  |  | Conc. ug/l | Conc. Mg/l | MDL
|  | at 1.0 mg/l |  | at 500 ug/l | 2 | 0.002 | 0.002 | 0.01 | 0.1
Discharge gallons/day | Million Gallons/day | Load/day (lbs) | load/yr (lbs) | load/yr (lbs) | 10 | 0.01 | at 5,000 gal/day load/yr =
2000 | 0.002 | 0.01668 | 6.0882 | 3.0441 | 50 | 0.05 | 0.030441 | 0.15221 | 1.5221
5000 | 0.005 | 0.0417 | 15.2205 | 7.6102 | 100 | 0.1
10000 | 0.01 | 0.0834 | 30.441 | 15.2205 | 200 | 0.2
15000 | 0.015 | 0.1251 | 45.6615 | 22.8307 | 300 | 0.3
20000 | 0.02 | 0.1668 | 60.882 | 30.441 | 400 | 0.4
25000 | 0.025 | 0.2085 | 76.1025 | 38.0513 | 500 | 0.5
30000 | 0.03 | 0.2502 | 91.323 | 45.6615 | 600 | 0.6
35000 | 0.035 | 0.2919 | 106.5435 | 53.2718 | 700 | 0.7
40000 | 0.04 | 0.3336 | 121.764 | 60.882 | 800 | 0.8
45000 | 0.045 | 0.3753 | 136.9845 | 68.4922 | 900 | 0.9
50000 | 0.05 | 0.417 | 152.205 | 76.1025 | 1000 | 1
100000 | 0.1 | 0.834 | 304.41 | 152.205 | 2000 | 2
Pounds/year | Million Gallons/yr | Gallons/yr
5 | 0.59952 | 599520.3837
10 | 1.199 | 1199040.7674
15 | 1.7986 | 1798561.1511
20 | 2.3981 | 2398081.5348
40 | 4.7962 | 4796163.0695
80 | 9.5923 | 9592326.1391
110 | 13.1894 | 13189448.4412

## WWTF Base
Facility:
TYPE OF PERMIT
Permit Number:
Permit Issue Date
Permit Expire Date
Facility Location:
SIC Code:
Facility Classification:
Facility Hydraulic Capacity:
Facility Organic Capacity:
Treatment Works:
Lift Stations:
Service Areas:
Compliance Schedules
Industrial Pretreatment Program
2014 Service Area Population Estimate:
2035 Service Area Population Estimate:
2014 Average Daily Effluent Treated:
Plant Expansion:
Discharge Point:
Waterbody Identification:
Receiving Water Designation (Segment):
Receiving Water Classification (Segment):
Treatened and Endangered Species
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | Aquatic life and temperature
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch,Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site

## 13 WLA
Bear Creek Watershed Wastewater Treatment Plants | Phosphorus Pounds/ year | 2013 Phosphorus Pounds/year | Percent of Allocation | WLA Phosphorus Pounds/ year |  | 2013 TP Lbs/Yr | 2012 TP Lbs/Yr | 2011 TP Lbs/Yr | 2010 TP Lbs/Yr | 2009 TP Lbs/Yr | 2008 TP Lbs/Yr | 2007 TP Lbs/Yr | 2006 TP Lbs/Yr | 2005 TP Lbs/Yr | 2004 TP Lbs/Yr | 2003 TP Lbs/Yr | 2002 TP Lbs/Yr | 2001 TP Lbs/Yr | 2000 TP Lbs/Yr | [7 empty] | Treatment Plant | TMAL Phosphorus | 2002 Phosphorus Pounds/ year
Evergreen Metropolitan District | 1500 | 332.28 | 22.15% | 1500 | Evergreen Metropolitan District | 332.28 | 251.62 | 199.46 | 274.23 | 235.5 | 245 | 380.31 | 453.1 | 631.4 | 664.6 | 694 | 743 | 627 | 721 | Treatment Plant | TMAL Phosphorus Pounds /Yr | 2004 Phosphorus Pounds/ year | Bear Creek Watershed Wastewater Treatment Plant | Phosphorus | 2008 Phosphorus |  |  | Pounds/ year
West Jefferson County Metro District | 1500 | 225.88 | 15.06% | 1500 | West Jefferson County Metro District | 225.88 | 168.92 | 215.89 | 278.69 | 374.7 | 506.7 | 799.41 | 616.11 | 676.34 | 592.4 | 696 | 926 | 904 | 744 | Evergreen Metropolitan District | 1500 | 1901-10-25 14:24 |  | Pounds/ year | Pounds/ year |  | Evergreen Metropolitan District | 1500 | 1902-01-12
Genesee Water and Sanitation District | 1015 | 319.64 | 31.49% | 1015 | Genesee Water and Sanitation District | 319.64 | 271.94 | 289.41 | 298.81 | 322.2 | 250.3 | 471.4 | 274.2 | 280.8 | 252.8 | 414 | 304 | 372 | 279 | West Jefferson County Metro District | 1500 | 1901-08-14 09:36 | Evergreen Metropolitan District | 1500 | 1900-09-01 |  | West Jefferson County Metro District | 1500 | 1902-07-14
Town of Morrison | 600 | 102.51 | 17.09% | 600 | Town of Morrison | 102.51 | 112.34 | 109.45 | 143.41 | 135 | 94 | 75 | 79 | 71 | 47 | 2142 | 116 | 115 | 99 | Genesee Water and Sanitation District | 1015 | 1900-09-08 19:12 | West Jefferson County Metro District | 1500 | 1901-05-20 16:48 |  | Genesee Water and Sanitation District | 1015 | 1900-10-30
Kittredge Sanitation and Water District | 240 | 76.24 | 31.77% | 240 | Kittredge Sanitation and Water District | 76.24 | 49.91 | 35.25 | 56.04 | 63.7 | 49.2 | 79.47 | 58.1 | 66.89 | 92 | 77.3 | 67 | 77 | 75 | Town of Morrison | 1901-08-22 |  | Genesee Water and Sanitation District | 1015 | 1900-09-06 07:12 |  | Town of Morrison | 1901-08-22 | 1900-04-25
Forest Hills Metropolitan District | 80 | 62 | 77.5% | 80 | Forest Hills Metropolitan District | 62 | 89.9 | 25.73 | 52.88 | 56.4 | 66.8 | 54.15 | 55.11 | 247.8 | 50.7 | 441 | 501 | 501 | 1701 | Kittredge Sanitation and Water District | 1900-08-27 | 1900-04-01 | Town of Morrison | 1901-08-22 | 1900-04-03 |  | Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-07
Conifer Metropolitan District/Conifer Sanitation Association | 80 | 0.88 | 1.1% | 80 | Conifer Metropolitan District/Conifer Sanitation Association | 0.88 | 13.05 | 1.42 | 1.92 | 5.1 | 8 | 0.51/3.65 | 2 | 7 | 11.3 | 12.8 | 6 | 4 | 15 | Forest Hills Metropolitan District | 1900-03-20 | 1900-02-18 16:48 | Kittredge Sanitation and Water District | 1900-08-27 | 1900-02-17 04:48 |  | Forest Hills Metropolitan District | 1900-03-20 | 1901-05-15
Aspen Park Metropolitan District | 40 | 5.07 | 12.68% | 40 | Aspen Park Metropolitan District | 5.07 | 9.52 | 6.94 | 9.65 | 6.4 | 12.8 | 3.64 | No Report | 5 | Not Operational | not operational | not operational | not operational | not operational | Conifer Center Sanitation Association | 1900-02-08 | 1900-01-10 07:12 | Forest Hills Metropolitan District | 1900-03-20 | 1900-03-06 19:12 |  | Conifer Center Sanitation Association | 1900-02-08 | 1900-01-05
Jefferson County Schools – Mt. Evans Outdoor Lab | 20 | 6.7 | 33.5% | 20 | Jefferson County Schools – Mt. Evans Outdoor Lab | 6.7 | 1.79 | 1.41 | 1.79 | 1.8 | 1.9 | 1.6 | 1.9 | 5.9 | 3 | 2.93 | 3.1 | 2 | no report | Aspen Park Metropolitan District | 1900-02-06 | Not Operational | Conifer Metropolitan District | 1900-03-20 | 1900-01-07 |  | Aspen Park Metropolitan District |  | not operational
Jefferson County Schools - Conifer High School | 110 | 1.66 | 1.509% | 110 | Jefferson County Schools - Conifer High School | 1.66 | 1.06 | 1.06 | 1.12 | 2.2 | 2.2 | 2 | 5.3 | 1.5 | 1.8 | 2.43 | 2.4 | 3 | 3 | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-04 | 1900-01-02 | Aspen Park Metropolitan District | 1900-02-08 | 1900-01-11 19:12 |  | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-04 | 1900-01-02 02:24
Bear Creek Cabins (Bruce & Jayne Hungate) | 5 | 1.81 | 36.2% | 5 | Bear Creek Development Corp. - Tiny Town | Hauling Columbia | 0.01 | 4.32 | 0.81 | 0.1 | 5 | 0.22 | No Report | No Report | no report | no report | no report | no report | no report | Jefferson County Schools - Conifer High School | 1900-05-04 | 1899-12-31 19:12 | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-19 | 1899-12-31 21:36 |  | Jefferson County Schools - Conifer High School | 1900-05-04 | 1900-01-01 09:36
Brook Forest Inn | 5 | 3.34 | 66.8% | 5 | Bear Creek Cabins (Bruce & Jayne Hungate) | 1.81 | 0.2 | 10.96 | 0.48 | 0.5 | no report | 0.52 | No Report | No Report | no report | no report | 53 | 33 | no report | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | no report | Jefferson County Schools - Conifer High School | 1900-04-19 | 1900-01-01 04:48 |  | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | no report
Geneva Glen1 | 5 |  | 0% | 5 | Brook Forest Inn | 3.34 | 1.66 | 8.01 | 1.58 | 48.2 | 1.5 | 4.1 | No Report | No Report | 0.5 | 12 | no report | no report | no report | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | no report | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | 1900-01-04 |  | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | 1900-02-21
Total Operational Facilities Lbs/year | 5200 | 1138.01 | 21.88% | 5 | Geneva Glen Camp | No Report | 0 | 0 | 0 | No Discharge | no report | No Discharge | No Report | No Discharge | Land Application | 4 | no report | no report | no report | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | 0.5 | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | no report |  | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | no report
Bear Creek Development Corp. - Tiny Town3 | 5 | Hauling Columbia |  | 18 | The Fort Resturant | No Monitoring | No Monitoring | No Monitoring | No Monitoring | No Monitoring | No Monitoring | No Monitoring | No Monitoring | No Monitoring | No Monitoring | No Monitoring | not operational | not operational | not operational | Geneva Glen | 1900-01-04 | Land Application | Brook Forest Inn | 1900-01-04 | 1899-12-31 12:00 |  | Geneva Glen | 1900-01-04 | no report
The Fort2 | 18 | No Monitoring |  | 30 | Singing River Ranch | Plugged | Plugged | Plugged | Plugged | Plugged | 0.1 | 1.3 | 3 | Out of Service | Out of Service | no report | no report | no report | no report | The Fort |  |  | Geneva Glen | 1900-01-04 | no report |  | The Fort2 |  | not operational
Singing River Ranch | 30 | Not Operational |  | 2 | Reserve Pool | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 625 | 625 | 100 | 100 | 100 | West/Brandt Foundation - Singing River Ranch | 1900-01-29 | Out of Service | The Fort | 1900-01-17 | No Monitoring2 |  | West/Brandt Foundation - Singing River Ranch | 1900-01-29 | no report
Reserve Pool | 2 | Not used 2013 | [17 empty] | Reserve Pool | 1900-04-09 | 1901-09-16 | Singing River Ranch | 1900-01-29 | 0.1 |  | Reserve Pool | 1900-04-09 | 1900-04-09
Total Phosphorus Wasteload lbs/year | 5255 | [21 empty] | Reserve Pool | 1900-01-01 | Not used
1-Geneva Glen treatment system land applies, dry lysimeters in 2013 and no phosphorus reported on DMRs | [19 empty] | Total Point Source Phosphorus Wasteload | 5,255 lbs/year | [5 empty] | Treatment Plant | TMAL Phosphorus | 2001 Phosphorus Pounds/ year
2-Permit; No established monitoring | [22 empty] | Treatment Plant | TMAL Phosphorus | 2003 Phosphorus Pounds/ year |  |  | Pounds/ year
3-Records from Columbia Sanitary show 35,000 gal hauled - .02 dry metric figured on 2% solids. | [19 empty] | Treatment Plant | TMAL Phosphorus | 2005 Phosphorus Pounds/ year |  | Pounds/ year |  |  | Evergreen Metropolitan District | 1500 | 1901-09-18
[21 empty] | Pounds/ year |  | Evergreen Metropolitan District | 1500 | 1901-11-24 |  | West Jefferson County Metro District | 1500 | 1902-06-22
2012 Phosphorus Pounds/ year | 2011 Phosphorus Pounds/ year | [18 empty] | Evergreen Metropolitan District | 1500 | 1901-09-22 09:36 | West Jefferson County Metro District | 1500 | 1901-11-26 |  | Genesee Water and Sanitation District | 1015 | 1901-01-06
1900-09-07 14:53 | 199.46 | [18 empty] | West Jefferson County Metro District | 1500 | 1901-11-06 08:10 | Genesee Water and Sanitation District | 1015 | 1901-02-17 |  | Town of Morrison | 1901-08-22 | 1900-04-24
1900-06-16 22:05 | 215.89 | [18 empty] | Genesee Water and Sanitation District | 1015 | 1900-10-06 19:12 | Town of Morrison | 1901-08-22 | 1905-11-11 |  | Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-17
1900-09-27 22:34 | 289.41 | [18 empty] | Town of Morrison | 1901-08-22 | 1900-03-11 | Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-17 07:12 |  | Forest Hills Metropolitan District | 1900-03-20 | 1901-05-15
1900-04-21 08:10 | 109.45 | [18 empty] | Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-06 21:22 | Forest Hills Metropolitan District | 1900-03-20 | 1901-03-16 |  | Conifer Center Sanitation Association | 1900-02-08 | 1900-01-03
1900-02-17 21:50 | 35.25 | [18 empty] | Forest Hills Metropolitan District | 1900-03-20 | (247.8)1 | Conifer Center Sanitation Association | 1900-02-08 | 1900-01-11 19:12 |  | Aspen Park Metropolitan District |  | not operational
1900-03-29 21:36 | 25.73 | [18 empty] | Conifer Town Center | 1900-02-08 | 1900-01-06 | Aspen Park Metropolitan District | 1900-02-06 | 1900-01-04 |  | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-04 | 1900-01-01
1900-01-12 01:12 | 1.42 | [18 empty] | Aspen Park Metropolitan District | 1900-02-08 | 1900-01-04 | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-04 | 1900-01-01 22:19 |  | Jefferson County Schools - Conifer High School | 1900-05-04 | 1900-01-02
1900-01-08 12:29 | 6.94 | [18 empty] | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-19 | 1900-01-04 21:36 | Jefferson County Schools - Conifer High School | 1900-05-04 | 1900-01-01 10:19 |  | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | NR2
1899-12-31 18:58 | 1.41 | [18 empty] | Jefferson County Schools - Conifer High School | 1900-04-19 | 1899-12-31 12:00 | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | NR2 |  | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | 1900-02-01
1899-12-31 01:26 | 1.06 | [18 empty] | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | No Report | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | NR3 |  | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | NR2
0.01 | 4.32 | [18 empty] | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | No Report | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | 1900-01-11 |  | Geneva Glen | 1900-01-04 | NR4
0.2 | 10.96 | [18 empty] | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | No Report | Geneva Glen | 1900-01-04 | 1900-01-03 |  | The Fort2 |  | not operational
1899-12-31 15:50 | 8.01 | [18 empty] | Geneva Glen | 1900-01-04 | no discharge | The Fort2 |  | No Monitoring |  | West/Brandt Foundation - Singing River Ranch | 1900-01-29 | NR2
0 | 0 | [18 empty] | The Fort | 1900-01-17 | no monitoring | West/Brandt Foundation - Singing River Ranch | 1900-01-29 | NR2 |  | Reserve Pool | 1900-04-09 | 1900-04-09
1902-08-28 22:05 | 909.31 | [18 empty] | West/Brandt Foundation - Singing River Ranch | 1900-01-29 | Out of Service | Reserve Pool | 1900-04-09 | 1901-09-16
No Monitoring | No Monitoring | [18 empty] | Reserve Pool | 1900-01-01 | Not used
Not Operational | Not Operational | [25 empty] | Treatment Plant | TMAL Phosphorus | 2000 Phosphorus Pounds/ year
Not used 2012 | Not used 2011 | [18 empty] | Total Point Source Phosphorus Wasteload | 5,255 lbs/year | 1680.44 | [5 empty] | Pounds/ year
1-Forest Hills Metro District no longer has an operational trade agreement. | 1 Forest Hills Metro District has trade agreement with West Jefferson County Metro District and complies with | [24 empty] | Evergreen Metropolitan District | Evergreen Metropolitan District | 1500 | 1901-12-21
2-Permit; No established monitoring | permit. 88.5 pounds was added into the West Jefferson County allocation, which was 190.21 pounds for a total West Jefferson County Metro District discharge of 278.69 pounds. | [18 empty] | Treatment Plant | TMAL Phosphorus | 2006 Phosphorus Pounds/ year |  |  |  | West Jefferson County Metro District | West Jefferson County Metro District | 1500 | 1902-01-13
3-The Geneva Glen treatment system land applies, dry lysimeters in 2012 and no phosphorus reported on DMRs | 2 Permit; No established monitoring | [19 empty] | Pounds/ year |  |  |  |  | Genesee Water and Sanitation District | Genesee Water and Sanitation District | 1015 | 1900-10-05
| 3 Brook Forest Inn reporting is under new owner/operator | [18 empty] | Evergreen Metropolitan District | 1500 | 1901-03-28 02:24 |  |  |  | Town of Morrison | Town of Morrison | 1901-08-22 | 1900-04-08
| 4 The Geneva Glen treatment system land applies, dry lysimeters | [18 empty] | West Jefferson County Metro District | 1500 | 1901-09-07 02:38 |  |  |  | Kittredge Sanitation and Water District | Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-15
[20 empty] | Genesee Water and Sanitation District | 1015 | 1900-09-30 04:48 |  |  |  | Forest Hills Metropolitan District | Forest Hills Metropolitan District | 1900-03-20 | 1904-08-27
[20 empty] | Town of Morrison | 1901-08-22 | 1900-03-19 |  |  |  | Conifer Metropolitan District/Conifer Sanitation Association | Conifer Center Sanitation Association | 1900-02-08 | 1900-01-14
[20 empty] | Kittredge Sanitation and Water District | 1900-08-27 | 1900-02-26 02:24 |  |  |  | Aspen Park Metropolitan District | Aspen Park Metropolitan District |  | not operational
[20 empty] | Forest Hills Metropolitan District | 1900-03-20 | 1900-02-23 02:38 |  |  |  | Jefferson County Schools – Mt. Evans Outdoor Lab | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-04 | NR
[20 empty] | Conifer Town Center | 1900-03-20 | 1900-01-01 |  |  |  | Jefferson County Schools - Conifer High School | Jefferson County Schools - Conifer High School | 1900-05-04 | 1900-01-02
[20 empty] | Aspen Park Metropolitan District | 1900-02-08 | No Report |  |  |  | Bear Creek Development Corp. - Tiny Town | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | no report
[20 empty] | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-19 | 1899-12-31 21:36 |  |  |  | Bear Creek Cabins (Bruce & Jayne Hungate) | Davidson Lodge | 1900-01-04 | no report
[20 empty] | Jefferson County Schools - Conifer High School | 1900-04-19 | 1900-01-04 07:12 |  |  |  | Brook Forest Inn | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | no report
[20 empty] | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | No Report |  |  |  | Geneva Glen1 | Geneva Glen | 1900-01-04 | no report
[20 empty] | Bear Creek Cabins (Bruce & Jayne Hungate)5 | 1900-01-04 | No Report |  |  |  | The Fort2 | The Fort2 |  | not operational
[20 empty] | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | No Report |  |  |  | Singing River Ranch | West/Brandt Foundation - Singing River Ranch | 1900-01-29 | no report
[20 empty] | Geneva Glen | 1900-01-04 | No Report 4 |  |  |  | Reserve Pool | Reserve Pool | 1900-04-09 | 1900-04-09
[20 empty] | The Fort | 1900-01-17 | No Report 5
[20 empty] | West/Brandt Foundation - Singing River Ranch | 1900-01-29 | 1900-01-02
[20 empty] | Reserve Pool | 1900-01-01 | Not used
[20 empty] | Total Point Source Phosphorus Wasteload | 5,255 lbs/year | 1904-03-21 19:12
[20 empty] | Treatment Plant | Phosphorus | 2007 Phosphorus Pounds/ year
Pounds/ year
[20 empty] | Evergreen Metropolitan District | 1500 | 1901-01-14 07:26
[20 empty] | West Jefferson County Metro District | 1500 | 1902-03-09 09:50
[20 empty] | Genesee Water and Sanitation District | 1015 | 1901-04-15 09:36
[20 empty] | Town of Morrison | 1901-08-22 | 1900-03-15
[20 empty] | Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-19 11:17
[20 empty] | Forest Hills Metropolitan District | 1900-03-20 | 1900-02-22 03:36
[20 empty] | Conifer Center Sanitation Association/ Conifer Town Center | 40/ 40 | 0.51/3.65
[20 empty] | Aspen Park Metropolitan District | 1900-02-08 | 1900-01-02 15:22
[20 empty] | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-19 | 1899-12-31 14:24
[20 empty] | Jefferson County Schools - Conifer High School | 1900-04-19 | 1900-01-01
[20 empty] | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | 0.22
[20 empty] | Bear Creek Cabins (Bruce & Jayne Hungate)5 | 1900-01-04 | 0.52
[20 empty] | Mary Ann Gallagher - Brook Forest Inn | 1900-01-04 | 1900-01-03 02:24
[20 empty] | Geneva Glen | 1900-01-04 | No Discharge3
[20 empty] | The Fort | 1900-01-17 | No Monitoring2
[20 empty] | Lost and Found Inc - Singing River Ranch | 1900-01-29 | 1899-12-31 07:12
[20 empty] | Reserve Pool | 1900-01-01 | Not used
[20 empty] | Total Point Source Phosphorus Wasteload | 5,255 lbs/year | 1904-03-21 19:12
[20 empty] | Bear Creek Watershed Wastewater Treatment Plant | Phosphorus | 2009 Phosphorus
[21 empty] | Pounds/ year | Pounds/ year
[20 empty] | Evergreen Metropolitan District | 1500 | 1900-08-22 12:00
[20 empty] | West Jefferson County Metro District | 1500 | 1901-01-08 16:48
[20 empty] | Genesee Water and Sanitation District | 1015 | 1900-11-17 04:48
[20 empty] | Town of Morrison | 1901-08-22 | 1900-05-14
[20 empty] | Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-03 16:48
[20 empty] | Forest Hills Metropolitan District | 1900-03-20 | 1900-02-24 09:36
[20 empty] | Conifer Metropolitan District | 1900-03-20 | 1900-01-04 02:24
[20 empty] | Aspen Park Metropolitan District | 1900-02-08 | 1900-01-05 09:36
[20 empty] | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-19 | 1899-12-31 19:12
[20 empty] | Jefferson County Schools - Conifer High School | 1900-04-19 | 1900-01-01 04:48
[20 empty] | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | 0.1
[20 empty] | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | 0.5
[20 empty] | Brook Forest Inn | 1900-01-04 | 1900-02-16 04:48
[20 empty] | Geneva Glen | 1900-01-04 | No Discharge3
[20 empty] | The Fort | 1900-01-17 | No Monitoring2
[20 empty] | Singing River Ranch | 1900-01-29 | Not Operational
[20 empty] | Reserve Pool | 1900-01-01 | Not used
[20 empty] | Bear Creek Watershed Wastewater Treatment Plant | Phosphorus | 2010 Phosphorus
[21 empty] | Pounds/ year | Pounds/ year
[20 empty] | Evergreen Metropolitan District | 1500 | 1900-09-30 05:31
[20 empty] | West Jefferson County Metro District | 1500 | 1900-10-04 16:34
[20 empty] | Genesee Water and Sanitation District | 1015 | 1900-10-24 19:26
[20 empty] | Town of Morrison | 1901-08-22 | 1900-05-22 09:50
[20 empty] | Kittredge Sanitation and Water District | 1900-08-27 | 1900-02-24 00:58
[20 empty] | Forest Hills Metropolitan District1 | 1900-03-20 | 1900-02-20 21:07
[20 empty] | Conifer Metropolitan District | 1900-03-20 | 1899-12-31 22:05
[20 empty] | Aspen Park Metropolitan District | 1900-02-08 | 1900-01-08 15:36
[20 empty] | Jefferson County Schools – Mt. Evans Outdoor School | 1900-01-19 | 1899-12-31 18:58
[20 empty] | Jefferson County Schools - Conifer High School | 1900-04-19 | 1899-12-31 02:53
[20 empty] | Bear Creek Development Corp. - Tiny Town | 1900-01-04 | 0.81
[20 empty] | Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | 0.48
[20 empty] | Brook Forest Inn3 | 1900-01-04 | 1899-12-31 13:55
[20 empty] | Geneva Glen4 | 1900-01-04 | 0
[20 empty] | Total Operational Facilities |  | 1903-01-25 09:50
[20 empty] | The Fort2 | 1900-01-17 | No Monitoring
[20 empty] | Singing River Ranch | 1900-01-29 | Not Operational
[20 empty] | Reserve Pool | 1900-01-01 | Not used 2010
[20 empty] | 35BTotal Phosphorus Wasteload | 5,255 lbs/year
Formulas:
The Fort2 = SUM(A27:[The Fort2, row above])

## 14 Planning Status
IFS15
Facility | Wastewater Utility Plan | Electronic Planning Documents | Recent Upgrades (3 yrs) | Facility Upgrades [2017-2022] | Existing Compliance Concerns1 | Informational Sheet
Evergreen Metropolitan District | Yes | WQCD Fact Sheet, WQA, Permit | Lift Station | Yes | TIN | IFS01
West Jefferson County | Yes | WQCD Fact Sheet, WQA, Permit | No | Yes | TIN | IFS03
Genesee | Yes | WQCD Fact Sheet, WQA, Permit | No | No | TIN | IFS04
Morrison | Yes | WQCD Fact Sheet, WQA, Permit | New WWTF | Yes | Mixing zone, Low Flows Bear Creek | IFS05
Kittredge | Yes | WQCD Fact Sheet, WQA, Permit | No | Yes | TIN | IFS02
Forest Hills Metropolitan District | Yes | Site Application Engineering Report, Permit (2009) | New WWTF | No | TP | IFS06
Conifer Metropolitan District | Yes | WQCD Fact Sheet, WQA, Permit | Yes, TDS | Yes | TDS | IFS08
Conifer Sanitation Association | Yes | Lift Station Rpt | Site Maintenance | Yes | No | IFS08
Aspen Park Metro District | Yes | WQCD Fact Sheet, WQA, Permit | Infiltration gallery, Outfall | Yes | Gallery Operation | IFS07
Jefferson County Schools Conifer High School | Yes | Site Application, Lift Station | Lift Stations, UV | Yes | Ammonia, TRC, UV | IFS10
Jefferson County Schools Mt Evan Outdoor | Yes | Site Application, New Plant Rpt | New WWTF | No | TP | IFS11
Bear Creek Development Corp. - Tiny Town | No | Land Application Rpt | Hauling Columbia | Yes | Reporting, WLA | No
Bear Creek Cabins | No | Permit | No | Closed Permit, Converted OWTS | No | Closed
Brook Forest Inn | No | WQCD Rational, WQA, Permit, Review | New upgrades | Yes | Reporting, WLA/TP, Compliance Order | IFS09
Geneva Glen | No | Permit, WQA, WQCD Fact Sheet | No | New Land Application | Reporting, WLA/TP, Compliance Order | In Progress
The Fort | Yes | Site Application, Closed | New OWTS | No | No | Closed
Singing River Ranch | No | WQCD Fact Sheet, WQA, Permit | No | Closed Permit, Converted OWTS | No | Closed
1 - All treatment facilities have expected new discharge limits (within 5-years) for total phosphorus and temperature. Several facilities are monitoring for temperature. Under Regulation 85 there are expected new nitrogen limits necessary to meet stream nitrogen standards.

## 15 Trade Facility
Bear Creek Watershed Wastewater Treatment Plants | Phosphorus Pounds/ year | 2013 Phosphorus Pounds/year | Eligible To Make Trades 2014-2015 | Eligible BCWA Trade Facility
Evergreen Metropolitan District | 1500 | 1900-11-27 06:43 | Yes | Yes
West Jefferson County Metro District | 1500 | 1900-08-12 21:07 | Yes | Yes
Genesee Water and Sanitation District | 1015 | 1900-11-14 15:22 | Yes | Yes
Town of Morrison | 1901-08-22 | 1900-04-11 12:14 | Yes | Yes
Kittredge Sanitation and Water District | 1900-08-27 | 1900-03-16 05:46 | Yes | Yes
Forest Hills Metropolitan District | 1900-03-20 | 62 | No | Yes
Conifer Metropolitan District/Conifer Sanitation Association | 1900-03-20 | 0.88 | Yes | Yes
Aspen Park Metropolitan District | 1900-02-08 | 1900-01-04 01:41 | Yes | Yes
Jefferson County Schools – Mt. Evans Outdoor Lab | 1900-01-19 | 6.7 | No | Yes
Jefferson County Schools - Conifer High School | 1900-04-19 | 1899-12-31 15:50 | Yes | Yes
Brook Forest Inn | 1900-01-04 | 1900-01-02 08:10 | No | Yes
Geneva Glen | 1900-01-04 | 1900-01-04 | No | Yes
Total Operational Facilities Lbs/year | 5195 | 1141.2
Bear Creek Cabins (Bruce & Jayne Hungate) | 1900-01-04 | 1899-12-31 19:26 | No - Closed Facility, Relinguishing State Discharge Permit | No
Bear Creek Development Corp. - Tiny Town | 1900-01-04 | Hauling Columbia | No | No
The Fort | 1900-01-17 | No Monitoring | No | Yes
Singing River Ranch | 1900-01-29 | Not Operational | No - Closed Facility, Relinguishing State Discharge Permit | No
Reserve Pool | 1900-01-01 | Not used 2013
Total Phosphorus Wasteload lbs/year | 5255

## 17 TP Trades
Involved Agencies | Type of Trade | Trading Activity | Active Trading
Forest Hills Metro District (FHMD) had trade agreement with West Jefferson County Metro District(WJCMD) | Point Source to Point Source | Discontinued in 2012 | No
City of Lakewood Coyote Gulch Project | Nonpoint source trade credits | Under data collection/ reviewed by Association; trade credit calculated in 2011- 2013/ confirmed 2014 | No
The Fort Restaurant | Reserve Pool to Point Source | Permit in Progress; Trade reflected in reserve pool limit previously granted by the WQCC; without permit no active trade | No
Jefferson County Schools (Conifer High School and Mt. Evans Outdoor School | Point Source to Point Source | In Discharge Permits; no change in pounds; reallocation between facilities | Yes
Conifer Metropolitan District/ Conifer Sanitation Association | Reserve Pool to Point Source | Trade reflected in reserve pool limit previously granted by the WQCC. CMD permit only shows 40 pounds; as such, 40 pounds remains designed to CSA | Yes
BCWA on Behalf of Small Minor Treatment Facilities - Policy Actions. BFI needs point to point trade. May also apply to Jefferson County Schools OutDoor Lab and Tiny Town | Point Source to Point Source | Policy 1 Trading Program; Policy 19 Nutrient Trading Program Eligiblity; BCWA Policy 26 - Point to Point Trade Administration | No

## 01 EMD
Evergreen Metro District
TYPE OF PERMIT | Domestic - Minor Municipal, Mechanical Plant, Sixth Renewal
Permit Number: | CO-0031429
Permit Issue Date | 2013-03-25
Permit Expire Date | 2018-03-31
Facility Location: | Evergreen Metropolitan District - wastewater treatment facility (WWTF) located at in the NE 1/4 of the NE 1/4 of S10, T5S, R71W; 27892 Meadow Drive in Evergreen, CO; at 39.635426° latitude North and 105.314337° longitude West
SIC Code: | 4952 Sewerage Systems
Facility Classification: | Class B per Section 100.5.2 of the Water and Wastewater Facility Operator Certification Requirements
Facility Hydraulic Capacity: | Based on Site Approval 1742, the design capacity of this domestic wastewater treatment works is 0.99 million gallons per day (MGD) for hydraulic flow (30-day average)
Facility Organic Capacity: | 2085 lbs. BOD5 per day for organic loading (30-day average)
Treatment Works: | The facility consist of a headworks, including bar screens, grit removal and influent flow measurements via a 9-inch Parshall flume equipped with ultrasonic meter, followed by a primary clarifier, chemical addition (sodium aluminate) for phosphorus removal, three aeration basins in series, a final clarifier, four sand filters, ultraviolet disinfection, and effluent flow measurement via a 9-inch Parshall flume equipped with ultrasonic meter.
Lift Stations: | 1900-01-03
Service Areas: | Evergreen Metropolitan District and Upper Bear Creek Association
Compliance Schedules | Conduct threshold tests for exclusion from further analysis under Mixing Zone Regulations. Total Inorganic Nitrate final limits.
Industrial Pretreatment Program | The pretreatment program includes a combination of the Kittredge WWTF District, the Evergreen WWTF District, and the West Jefferson County WWTF District. It was established in 2001.
2014 Service Area Population Estimate: | 6,670 (Taps Served 2,615), See BCWA Fact Sheet 41 Wastewater Demographics and BCWA Fact Sheet 26 Watershed Demographics
2035 Service Area Population Estimate: | 7,500 (no major expansion of service area planned, system near build-out)
2014 Average Daily Effluent Treated: | 0.52/0.42/0.96 (Avg/Min/Max)
Plant Expansion (5-year): | None planned
Discharge Point: | Bear Creek - 001A following disinfection and prior to mixing with the receiving stream. Mixing zone.
Mixing Zone: | The WWTF is not exempt from the need for a mixing zone analysis, as the ratio of the facility design flow to the chronic low flow (30E3) is equal to 0.68:1, while the ratio of the chronic low flow to the design flow is equal to 1.5:1.
Waterbody Identification: | Bear Creek at 39.635° N, 105.309° W.
Receiving Water Designation: | COSPBE01e, Bear Creek
Receiving Water Classification: | Aq. Life Cold 1,Rec. Class E, Ag., Water Supply
Treatened and Endangered Species | No
Colorado WQCC Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers to the creek. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 1,500 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | Aquatic life and temperature
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch, Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | http://www.evergreenmetrodistrict.com/

## 02 West Jeff
TYPE OF PERMIT | Domestic-Minor Municipal, Mechanical Plant, Sixth Renewal
Permit Number: | CO 0020915
Permit Issue Date | 2/28/2013
Permit Expire Date | 3/31/2018
Facility Location: | West Jefferson WWTF located at in the NE ¼ of the NE1/4 of S33, T4S, R71W; 29847 Lewis Ridge Road, Evergreen, CO; at 39.6628° latitude North and 105.3352° longitude West
SIC Code: | 4952 Sewerage System
Facility Classification: | Class B per Section 100.5.2 of the Water and Wastewater Facility Operator Certification Requirements
Facility Hydraulic Capacity: | 0.7 MGD
Facility Organic Capacity: | 1,798 lbs BOD/day
Treatment Works: | The facility consist of a headworks, including bar screens, grit removal and influent flow measurements via a 9-inch Parshall flume equipped with ultrasonic meter, followed by chemical addition (sodium aluminate) for phosphorus removal, three aeration basins in series, two final clarifier, two sand filters, ultraviolet disinfection, and effluent flow measurement via a 9-inch Parshall flume equipped with ultrasonic meter.
Lift Stations: | 5
Service Areas: | West Jefferson County Metropolitan District
Compliance Schedules | a. A compliance schedule to give the facility time to install the appropriate temperature monitoring equipment and begin gathering information
b. A compliance schedule to give the facility time to complete a mixing zone analysis and report findings to the Division. A timeframe of two years has been established to meet this requirement.
c. A compliance schedule to give the facility time to install any necessary construction or additional treatment to meet newly established T.I.N. limitations. A timeframe of five and a half years has been established to meet this requirement. If the limitations can be met with the current treatment process, no construction is required.
Industrial Pretreatment Program | The pretreatment program includes a combination of the Kittredge WWTF District, the Evergreen WWTF District, and the West Jefferson County WWTF District. It was established in 2001.
2013 Service Area Population Estimate: | 6,600 (2,593 Taps) See BCWA Fact Sheet 41 Wastewater Demographics and BCWA Fact Sheet 26 Watershed Demographics
2035 Service Area Population Estimate: | 7,000 (no major expansion of service area planned, system near build-out)
2013 Average Daily Effluent Treated: | 0.4657/0.3010/0.9611 (Avg/Min/Max)
Plant Expansion (5-years): | None planned
Discharge Point: | 001A, following disinfection and prior to mixing with the receiving stream. 39.6632 °N, 105.3352° W
Waterbody Identification: | Troublesome 39.6631 °N, 105.3347 ° W
Receiving Water Designation (Segment): | COSPBE05, Troublesome Gulch
Receiving Water Classification (Segment): | Aq. Life Cold 1, Rec. Class E, Ag.,Water Supply
Threatened and Endangered Species | No
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 1,500 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | Aquatic life and temperature
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch,Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.

## 03 Kittredge
TYPE OF PERMIT | Domestic – Minor Municipal, Mechanical Plant
Permit Number: | CO 0023841
Permit Issue Date | 2013-03-26
Permit Expire Date | 2018-03-31
Facility Location: | Kittredge Water and Sanitation District
Latitude: 39.6887° N, Longitude: 105.2875°W
SIC Code: | 1913-07-22
Facility Classification: | Class B per section 100.9.2 of the regulations for Water and Wastewater facility Operator Certifications requirements
Facility Hydraulic Capacity: | 0.125 MGD
Facility Organic Capacity: | 398 lbs. BOD/Day
Treatment Works: | The facility consist of a headworks, including bar screens, grit removal and influent flow measurements via a 3-inch Parshall flume equipped with ultrasonic meter, followed by chemical addition (sodium aluminate) for phosphorus removal, one aeration basins, a final clarifier, . ultraviolet disinfection, flow through a polishing pond, and effluent flow measurement via a 3-inch Parshall flume equipped with ultrasonic meter.
Lift Stations: | None
Service Areas: | Kittredge Water and Sanitation District
Compliance Schedules | A compliance schedule to give the facility time to complete a mixing zone analysis and report findings to the Division. A timeframe of two years has been established to meet this requirement. A compliance schedule to give the facility time to install any necessary construction or additional treatment to meet newly established T.I.N. limitations. A timeframe of five and a half years has been established to meet this requirement. If the limitations can be met with the current treatment process, no construction is required
Industrial Pretreatment Program | The pretreatment program includes a combination of the Kittredge WWTF District, the Evergreen WWTF District, and the West Jefferson County WWTF District. It was established in 2001.
2013 Service Area Population Estimate: | 1,218 with 478 taps, See BCWA Fact Sheet 41 Wastewater Demographics and BCWA Fact Sheet 26 Watershed Demographics
2035 Service Area Population Estimate: | 1,400 (no major expansion of service area planned, system near build-out)
2013 Average Daily Effluent Treated: | 0.0439/0.018/0.2222 (Avg/ Min/ Max)
Plant Expansion (5-years): | None Planned
Discharge Point: | 001A, following disinfection and prior to mixing with receiving stream. Latitude 39.652993 Longitude 105.1777171
Waterbody Identification: | Bear Creek
Receiving Water Designation (Segment): | COSPBE01e, Bear Creek
Receiving Water Classification (Segment): | Aq. Life Cold 1,Rec. Class E, Ag., Water Supply
Threatened and Endangered Species | No
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 240 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | Aquatic life and temperature
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch,Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site

## 04 Genesee
TYPE OF PERMIT | Domestic – Minor Municipal, Mechanical Plant
Permit Number: | CO-0022951
Permit Issue Date | April 14, 2008
Permit Expire Date | June 1, 2013
Facility Location: | NE ¼ of the SW ¼ of S30, T4S, R70W, 6th PM; 2310 Bitterroot Ln, Golden, CO 80401 at 39-40-34 latitude North and 105-16-26 longitude West
SIC Code: | 4952 Sewerage Systems
Facility Classification: | Class B
Facility Hydraulic Capacity: | 0.80 MGD
Facility Organic Capacity: | 1,340 lbs. BOD per day (30 day average)
Treatment Works: | Headworks (screening , grit removal, flow monitoring), magnesium hydroxide addition for alkalinity/pH, Two treatment trains (MLE Process), sodium aluminate for phosphorus removal, secondary clarifiers, gaseous chlorine disinfection, chlorine contact chambers, sodium thiosulfate de-chlorination, effluent flow monitoring.
Lift Stations: | 4
Service Areas: | Genesee Water & Sanitation District. The District’s service area stretches from slightly north of Interstate Highway 70 to Bear Creek on the south, and contains approximately 2,870 acres. Within the District there are 1,270 single and multi-family users and approximately 30 commercial users, including retail, restaurants, churches, schools and recreational facilities
Compliance Schedules | none
Industrial Pretreatment Program | Grease Trap Program – No industrial customers
2013 Service Area Population Estimate: | Population 3,699, Population Served 4,040. 1,592 EQRs. See BCWA Fact Sheet 41 Wastewater Demographics and BCWA Fact Sheet 26 Watershed Demographics
2035 Service Area Population Estimate: | 4,200. Very minimal growth potential. (no major expansion of service area planned, system near build-out)
2013 Average Daily Effluent Treated: | 0.246 MGD
Plant Expansion (5-years): | None planned
Discharge Point: | Outfall 001A, following the chlorine contact chamber and prior to entering the unnamed tributary to Bear Creek
Waterbody Identification: | Discharged to unnamed gulch which is a tributary of Bear Creek
Receiving Water Designation (Segment): | COSPBE04A
Receiving Water Classification (Segment): | Class 2, Aquatic Class 1, Cold Water, Water Supply & Agricultural Stream
Threatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | 1,015 lbs/yr
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | Aquatic life and temperature
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch,Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.
Web Site | http://www.geneseewater.com/

## 05 Morrison
IFS05
Facility: Morrison Water Reclamation Facility
TYPE OF PERMIT | Domestic-Minor Municipal, Mechanical Plant, Renewal
Permit Number: | CDPS Permit No.: CO-0041432
Permit Issue Date | 7-24-09
Permit Expire Date | Applied for a new 5 yr permit 4-22-14
Facility Location: | Intersection of C-470 and Morrison Rd - NE corner. SE1/4 of SW1/4, Sec 36, T4S, R7OW. Latitude 39.65435 Longitude 105.1798
SIC Code: | 4952 Sewerage System
Facility Classification: | Class B per Section 100.5.2 of the Water and Wastewater Facility Operator Certification Requirements
Facility Hydraulic Capacity: | 0.35 MGD (Peak Hour Hydraulic Capacity 1.05 MGD)
Facility Organic Capacity: | 876 lbs. BOD5/day
Other Permit Parameters: | TSS = 30 mg/l (30-day average), Total Ammonia (monthly) ranges from 19-40 mg/l, E. coli = 1,290 cts/100ml, Temperature report, BOD5 (30-day average) = 30 mg/l
Treatment Works: | A new Sequencing Batch Reactor facility was put on line 9/25/2013. It includes a mechanically cleaned fine screen (1/4"openings) with a screening washer press (with a manual bar screen provided as backup), a 3-inch Parshall flume (within a 9-inch Parshall flume), ultrasonic flow sensing, a mechanical vortex grit chamber, grit pump, and grit classifier. After screening, grit removal, and odor scrubbing uses granular activated carbon, a lift station with three pumps (using variable frequency drives for energy efficiency) pumps flow to parallel Sequencing Batch Reactor basins. Each basin includes a pre-react zone and a combination aerobic/anoxic/settling zone. Cycling of fine bubble aeration and anoxic treatment with predetermined settling and decanting periods provides robust nitrification, denitrification, and clarification. After clarification, two fully redundant ultraviolet light (UV) contactors are used to disinfection the water before discharge into Bear Creek.
Lift Stations: | None
Service Areas: | Town of Morrison, City and County of Denver Red Rocks (Contract), Mt. Carbon.
Compliance Schedules | none
Industrial Pretreatment Program | There are no categorical discharges, but discharges with significant volumes are regulated pursuant to the Town Code section 8-3
2014 Service Area Population Estimate: | 433 (243 EQR)
2035 Service Area Population Estimate: | An additional 100 residential EQRs + 80 commercial EQRs west of the Hogback, and as many as another 2,300 EQRs in the Mount Carbon Metro District (NE of the intersection of C-470 and Morrison Road). The Utility Plan assumes 3 people per residential EQR.
2014 Average Daily Effluent Treated: | .071 MGD
Plant Expansion: | New plant completed in 2013; no other plant expansions planned
Discharge Point: | As shown in permit - 001A, Latitude 39° 39’ 11.27”N, Longitude 105° 10’ 39.78”W; Outfall at Latitude 39.652993, Longitude -105.177171
Waterbody Identification: | Bear Creek, Mainstem of Bear Creek from Harriman Ditch to the inlet of Bear Creek Reservoir
Receiving Water Designation (Segment): | COSPBE01 B, Bear Creek.
Receiving Water Classification (Segment): | Aq. Life Cold 2, Recreation E, Water Supply, Agriculture
Threatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 600 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | Biological Oxygen Demand, Total Suspended Solids, E. coli, phosphorus, ammonia, nitrogen, and temperature
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch, Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.
BCWA Factsheets | BCWA Factsheet 34 - New Morrison Water Reclamation Facility, BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | http://town.morrison.co.us/

## 06 Forest Hills
Facility: Forest Hills Metropolitan District
TYPE OF PERMIT | Domestic – Minor Municipal, Mechanical Plant
Permit Number: | Permit No. CO-0037044
Permit Issue Date | 39196
Permit Expire Date | 8/1/2012 (Administrative extension)
Facility Location: | NE 1/4, SW 1/4, Section 17, T4S, R70W; 39° 42' 09" N, 105° 15' 07" W
SIC Code: | 4952
Facility Classification: | Class C per Section 100.5.2 of the Water and Wastewater Facility Operator Certification Requirements
Facility Hydraulic Capacity: | 0.05 million gallons per day (MGD) for hydraulic flow (30-day average)
Facility Organic Capacity: | 96 lbs. BOD5 per day for organic loading (30-day average)
Treatment Works: | Existing Plant: Ultrasonic INF flow meter, bar screen, 50K Fluidyne SBR plant, EFF tank/ with pumps to discharge, chlorination, dechlorination, ultrasonic EFF meter. Sludge removal via pumping ISAM tank of SBR. As Defined in Permit: The existing WWTP is located at on the northeast corner of the service area. The current Discharge Permit is valid until August 31, 2012. The rated capacity is 50,000 gpd and is currently receiving approximately 20,000 gpd. The following summary of the treatment components are based on the Discharge Permit, operating documents and field observations. Provided below is a summary of the treatment process: 1. Raw sewage screen, 2. Equalization tank with a single discharge pump, 3. Anaerobic tank (1,100 gallon), 4. Anoxic tank (1,100 gallon), 5. Rotating Biological Contactor (RBC), 6. Clarifier, 7. Disinfection, 8. Chlorine Contact Chamber, 9. Parshall flume, 10. Dechlorination, 11. Discharge, 12. Digester
Lift Stations: | The District has two lift stations: Lift Station #1 and the Panorama Lift Station. Both service a small portion of the collection system and discharge into a gravity sewer line that flows to the existing WWTP. The existing sewer lines are adequately sized to convey current average day and peak hour flows. It consists of 8” PVC lines and two forces mains, one from each lift station.
Service Area: | It is comprised of approximately 145 single-family residential homes. The District does not have any multi-family residential, office, school or commercial uses. It does have one small park area. there are no future plans to expand the service area boundary beyond its current limits. There are approximately five vacant lots within the District that could be developed.
Compliance Schedules | TRC, ammonia and phosphorous; no longer entered into trade agreement for Total Phosphorus; some compliance problems with new plant at start-up, now corrected.
Industrial Pretreatment Program | None
2014 Service Area Population Estimate: | 375 (150 Taps served)
2035 Service Area Population Estimate: | 400 (Limited taps left and no plans for expansion)
2014 Average Daily Effluent Treated: | 0.021 MGD
Plant Expansion: | None planned; New treatment facility.
Discharge Point: | Outfall 001A, following disinfection and prior to mixing with the receiving stream.
Waterbody Identification: | Mt. Vernon Creek
Receiving Water Designation (Segment): | 4a, All tributaries to Bear Creek, including all wetlands, from the outlet of Evergreen Lake to the confluence with the South Platte River, except for specific listings in Segments 5, 6a, and 6b.
Receiving Water Classification (Segment): | Aq Life Warm 2, Recreation E, Water Supply, Agriculture
Threatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 80 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch, Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Wed Site | http://www.fhmd.net/

## 07 Aspen Park
Facility: Aspen Park Metropolitan District
TYPE OF PERMIT | Domestic – Minor Municipal, Mechanical Plant, New
Permit Number: | Old Number CO-0631016; Changed to CO-000001.
Permit Issue Date | 41164
Permit Expire Date | 43039
Facility Location: | Aspen Park MD wastewater treatment plant located at 25517 Conifer Road, Conifer, CO 80433, in the NE 114 of the SW 114 ofS12, T6S, R71W; at 39.544° latitude North and 105.286° longitude West
SIC Code: | 4952 Sewerage Systems
Facility Classification: | Class B per section 100.9.2 of the regulations for Water and Wastewater facility Operator Certifications requirements
Facility Hydraulic Capacity: | Based on Site Approval 4683, the design capacity of this domestic wastewater treatment works is 0.025 million gallons per day (MGD) for hydraulic flow (30-day average)
Facility Organic Capacity: | 104 lbs. BOD5 per day for organic loading (30-day average)
Treatment Works: | The facility consists of a microstrainer and bar screen, equalization basin, anoxic basin, Zenon membrane, and then UV disinfection with the discharge then going to exfiltration gallery’s #1 and #2. Any flow not absorbed in the exfiltration basins will then be discharged to South Turkey Creek.
Major Changes to Treatment Works | The Aspen Park MD WWTF had an existing permit (COX0046591) to discharge solely to groundwater. However, the exfiltration galleries for the groundwater discharge were not able to keep up with the effluent flows to the WWTF. The district intends to continue using the exfiltration galleries to the extent possible to fulfill groundwater augmentation requirements while discharging any water to South Turkey Creek that is not exfiltrated by these galleries. Therefore, the district added a new discharge point to surface water (e.g. South turkey Creek). This new discharge point is a reviewable segment so antidegradation considerations apply to this new surface water discharge point. The district worked with the Division on an Alternatives Analysis (AA) as outlined and explained in the Preliminary Effluent Limitations for the new discharge to South Turkey Creek. To protect all receiving waters the effluent limits in this permit is protective of both groundwater, and WQBELS and ADBELs for surface water in South Turkey Creek.
Lift Stations: | There are no lift stations in the service area.
Service Areas: | The Aspen Park MD treats domestic sewage from the King Soopers shopping center area. See BCWA Policy 9 - Aspen Park Wastewater Strategy for defined service area.
Compliance Schedules | Install Influent Monitoring, August 31, 2013
Industrial Pretreatment Program | See permit requirements
2014 Service Area Population Estimate: | 11 EQRs. Retail, 11 businesses (150 non-transients and 1,500 Transients/day, yearly average)
2035 Service Area Population Estimate: | South Turkey Creek Regional Plant operated by the Aspen Park Metropolitan District (Wastewater Utility Plan November 2004 and February 2008). This plant can expand to serve all viable commercial interest in the South Turkey Creek drainage, Aspen Park area.
2014 Average Daily Effluent Treated: | 0.014 MGD
Plant Expansion: | Defined in wastewater utility plan with expectation to expand to 0.05 MGD before 2035. None planned in next five-years.
Discharge Point: | Groundwater and surface water discharge (South Turkey Creek); 001A following disinfection and prior to mixing with groundwater or surface receiving waters 39° 32' 34.10" N, 105° 17' 8.94"W. 002A for effluent flow only, following exfiltration galleries and prior to mixing with surface receiving waters.
Waterbody Identification: | South Turkey Creek and Groundwater
Receiving Water Designation (Segment): | COSPBE06a, South Turkey Creek; Turkey Creek system, including all tributaries and wetlands, from the source to the inlet of Bear Creek Reservoir, except for specific listings in Segment 6b.
Receiving Water Classification (Segment): | Aq Life Cold 2, Recreation E, Water Supply, Agriculture
Threatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 40 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 0.5 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | Phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 12-28-2011 Assessment completed for PEL200172, Revised effluent limitations for the Aspen Park Metropolitan District WWTF based on an Alternatives Analysis for the District for a surface water discharge to South Turkey Creek, and continuing discharge to groundwater. WQCD Fact Sheet available.
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | Aspenparkmetropolitandistrict.org

## 08 CMD & CSA
Facility: Treatment Plant Conifer Metropolitan District; Lift Station serves separate service area for Conifer Sanitation Association
Conifer Sanitation Association Lift Station: | A lift station and force main connect the Conifer Sanitation Association (CSA) to the Conifer Metropolitan District (CMD) or the Conifer Town Center for wastewater service. The wastewater distribution system requires a return flow of treated wastewater from the CMD treatment plant back upstream to the CSA discharge point because of the water rights decree. As such, the CSA will own and operate the lift station and force main. CSA has a fixed the capacity of 19,000 gpd. The total service area of the CSA is approximately 61 acres. The CSA facility consists of a 20-gpm lift station and force main that conveys the entire sewage volume from the current CSA plant site for treatment at the regional CMD facility. The grinder pumps have a capacity of 20 gpm each, which is greater than the average equalized influent rate of 13.1 gpm. This will provide a conservative pumping rate of 35% above the average influent flow rate. The lift station will operate automatically with a float mechanism provided by ABS to trigger operation. The pumps will be able to pump the entire influent flow rate independently of each other providing a 100% redundancy. A 7’-6” diameter precast manhole, which serves as the wet well on the existing CSA site. This manhole will have an interior depth of 10 ft. The wet well will have a working depth of 5.2 ft. It has a working volume of 1,833 gallons, equal to 28 minutes of the peak influent flow rate. Overflow containment is stored in three existing 6,000-gallon tanks on site, which will provide an additional 3-3/4hrs of emergency storage at peak flow rates. This provides a 4 hr emergency response time to the facility at peak flow rates, and 20 hrs at the average flow rate.
TYPE OF PERMIT - CMD | Domestic - Minor Municipal, Mechanical Plant; Domestic Minor, Renewal Groundwater-State Permitting Only
Permit Number: | CSA - COX-047392; CMD COG589060
Permit Issue Date | 41631
Permit Expire Date | 43496
Facility Location: | NW 1/4 of SE 1/4 of Section 41, Township 6 South, Range 71 West; Sixth Principal Meridian; Jefferson County. The WWTF is located at 10420 South US Highway 285, Conifer, Colorado 80433
SIC Code: | 4952 Sewerage Systems
Facility Classification: | Class B per Section 100.5.2 of the Water and Wastewater Facility Operator Certification Requirements
Facility Hydraulic Capacity: | 0.0435 Million Gallons per Day (MGD)
Facility Organic Capacity: | 251 lbs. BOD5 per day for organic loading (30-day average).
Treatment Works: | The CMD consists of the following treatment processes: Influent and effluent flow measurement will be measured by a 6-inch magmeter and recorder; Preliminary treatment will be provided by a mechanical rotary screen with 2 millimeter (mm) slot openings; Secondary treatment will be provided by two separate parallel trains each consisting of an 15,000-gallon anoxic basin, 33,150-gallon complete mix aeration basin, and the clarification shall be provided by two Zenon ultra filtration membrane units; Disinfection will be provided by redundant Aquafine ultraviolet light system; An effluent pump station fitted with two 50 gallon per minute (gpm) pumps shall convey treated effluent to the exfiltration gallery for discharge to groundwater; The exfiltration gallery consists of approximately 12,000 square feet of recharge area divided into four separate areas for independent dosing; Biosolids shall be stabilized by two 33,150-gallon aerobic digesters and disposed of by a local land application.
Service Areas: | Conifer Metropolitan District North Turkey Creek Regional Wastewater Treatment Plant Utility Plan. See BCWA Policy 9 - Aspen Park Wastewater Strategy for defined service area.
Compliance Schedules | None
Chloride Variance | The Water Quality Control Division (Division) has granted a “variance” to this facility because it cannot comply with the chloride effluent limitation of 250 mg/L. The source of chloride is either the raw water and/or chemical addition used to improve the quality of the drinking water, e.g., drinking water treatment or water softeners. This renewal permit will include a “Report Only” for chloride.
Groundwater Classification for CMD Discharge | Groundwater below Conifer Metropolitan District WWTF does not have a "site-specific" classification. The Division shall implement the Interim Narrative Standards that are in "The Basic Standards for Ground Water" (Regulation # 41) to establish ground-water protection. The groundwater standards are included in Regulation No. 41, Tables 1 through 4. These numeric standards are utilized to establish compliance limitations. Compliance limitations shall be at the point of discharge (subsequent to treatment) and prior to subsurface discharge, identified in the permit as 001A.
Industrial Pretreatment Program | None
2014 Service Area Population Estimate: | CMD - 10 EQRs, Retail, 10+ businesses (1,250 Transients/day, Yearly Average); CSA - 4 EQRs, Retail, 4+ businesses (450 Transients/day, Yearly Average)
2035 Service Area Population Estimate: | No population estimates; retail EQRS fixed for CSA and could expand to 20 EQRs for CMD
2014 Average Daily Effluent Treated: | 0.0039 MGD
Plant Expansion: | None planned
Discharge Point: | Outfall 001A: following disinfection and prior to discharge to groundwater. Lattitude: 39° 31' 49.83″ North, Longitude: 105° 18' 17.21″ West
Waterbody Identification: | North Turkey Creek
Receiving Water Designation (Segment): | CSA - 6b, Mainstem of North Turkey Creek, from the source to the confluence with Turkey Creek. CMD - Groundwater
Receiving Water Classification (Segment): | Aq Life Cold 1, Recreation E, Water Supply, Agriculture
Treatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | The CMD permit only lists 40 pounds of total phosphorus. The actual cumulative annual limitation is 80 pounds of total phosphorus; The Association recommended the 40 annual pounds total phosphorus allocation assigned to the Conifer Sanitation Association in the Control Regulation be assigned to the Conifer Metropolitan District for a total allocation to the CMD of 80 pounds.
Control Regulation #74 Total Phosphorus Limit | 0.5 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 12-23-2013 factsheet completed for CMD; Liftstation report available for CSA
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | none for either CMD or CSA

## 09 BFI
Facility: Historic Brook Forest Inn
TYPE OF PERMIT | Domestic- Minor Municipal, Mechanical Plant
Permit Number: | CO-0030261
Permit Issue Date | 39475
Permit Expire Date | Renewal application submitted 4-21-2014
Facility Location: | NW ¼ of NW ¼ of S31, T5S, R71W; at 8136 South Brook Forest Road in Evergreen, CO; at 39.579394° latitude North and 105.380764° longitude West.
SIC Code: | 4952 Sewerage Systems
Facility Classification: | Class B per Section 100.5.2 of the Water and Wastewater Facility Operator Certification Requirements
Facility Hydraulic Capacity: | 0.009 MGD
Facility Organic Capacity: | 18 lbs BOD5/day
Treatment Works: | The facility consists of an aeration basin, clarifier, and chlorine contact basin. An alum injection system has been installed for phosphorus removal. Influent flow is based on the water meter equipped with a totalizer. Effluent flow is measured by a 90° V-notch weir equipped with a totalizer. Division records show that the facility obtained site approval on July 6, 1976 under site application approval No. 2066. Because a hardcopy of site approval letter No. 2066 is not available for review, the approved hydraulic capacity of 0.009 MGD and approved organic capacity of 18 lbs BOD5/day provided in this permit are based upon the rationale for the previous permit.
Lift Stations: | There are no lift stations in the service area.
Service Areas: | Brook Forest Inn and property only
Compliance Schedules | The data shown in the preceding tables indicates that the Brook Forest Inn WWTF has exceeded permit limits on several occasions including one exceedance each of the May ammonia monthly average, the BOD5 monthly average and the BOD5 percent removal limits. There were two exceedances each of the TSS monthly average and the TSS percent removal limits, and three exceedances of the TSS weekly average limit. Finally, there have been five exceedances of the total phosphorous monthly average limit. Total phosphorus compliance being addressed through trading.
Industrial Pretreatment Program | None
2014 Service Area Population Estimate: | 1 EQR; Hotel 16 rooms, Resturant 60+ seats, Pub, Special Events
2035 Service Area Population Estimate: | Fixed EQR, no expectation of growth or change in use
2014 Average Daily Effluent Treated: | 0.0008 MGD
Plant Expansion: | Plant upgrades necessary in 5-years
Discharge Point: | 001A, following the chlorine contact chamber and before entering Cub Creek.
Waterbody Identification: | Cub Creek
Receiving Water Designation (Segment): | The permit lists the wrong stream segment as 3. The correct stream segment is 5, Swede, Kerr, Sawmill, Troublesome, and Cold Springs Gulches, and mainstem of Cub Creek from the source to the confluence with Bear Creek.
Receiving Water Classification (Segment): | The WQCD used the wrong cold water classification (life cold 1) as part of the WQA; the correct classiciations are Aq Life Cold 2, Recreation E, Water Supply, Agriculture
Threatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 5 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed WQA for BFI January 28, 2008
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | http://www.thebrookforestinn.com/

## 10 Jeffco High
Facility: Jefferson County Public Schools - Conifer High School
TYPE OF PERMIT | Domestic-Minor Municipal, Mechanical Plant
Permit Number: | CO-047988
Permit Issue Date | 39931
Permit Expire Date | 5/31/2014
Facility Location: | in the N ½ of the SW ¼ of Section 14 and the N ½ of the SE ¼ of Section 15, T6S, R71W; at 10441 County Highway 73, Conifer, CO 80433 at 39º31’81” latitude north and 105º18’62” longitude West
SIC Code: | 4190
Facility Classification: | Class B
Facility Hydraulic Capacity: | 0.052 MGD (Peak Hourly .077 MGD)
Facility Organic Capacity: | 220 lbs. /day
Treatment Works: | Raw sewage entering the treatment facility is first screen before entering a flow equalization/ anoxic basin. Variable speed, submersible pumps are used to transfer wastewater from the flow equalization /anoxic basin to the aeration basin at a constant flow rate. The anoxic basin is used for biological denitrification and the aeration basin provides nitrification and CBOD removal by the extended aeration activated sludge treatment process. A flocculating clarifier is provided to allow phosphorous removal by addition of alum. Additional treatment is provided denitrifying filter and a solids removal filter. Prior to discharge, disinfection by long duration contact with sodium hypochlorite is provided. Effluent wastewater flow is recorded and totalizer using a 90º V-notch weir.
Lift Stations: | WJE, WJM, Conifer WTP, 3 total
Service Areas: | Jefferson County Public Schools in the Conifer articulate area. 2 elementary schools, 1 Middle school, 1 High school. The facility also receives minor flows from both the west transportation facility and the District’s water treatment plant. The District’s wastewater collection system receives direct flows from Conifer High and West Jefferson Middle and Elementary school. Conifer High flows by gravity to the plant where West Jefferson Middle and Elementary flows are pumped through two lift stations and a force main. Sewage truck loads from Marshdale Elementary and west area transportation facility are discharged three times a week (i.e. Monday, Wednesday and Friday).
Compliance Schedules | Activities to meet Ammonia and TRC. Replace the chlorination/dechlorination Disinfection system with Ultraviolet Light Disinfection.
Industrial Pretreatment Program | None
2013 Service Area Population Estimate: | 5 tabs at 2,400 EQR. 5 facilities, 2,100 studens + staff (Primarily school sessions only)
2035 Service Area Population Estimate: | No expected increase in EQRs
2013 Average Daily Effluent Treated: | 5,000 gpd
Plant Expansion: | None
Discharge Point: | Outfall 001A, following disinfection and prior to entering Lobo Creek, which is tributary to North Turkey Creek
Waterbody Identification: | Lobo Creek
Receiving Water Designation (Segment): | 6b Mainstem of North Turkey Creek, from the source to the confluence with Turkey Creek.
Receiving Water Classification (Segment): | Aq Life Cold 1, Recreation E, Water Supply, Agriculture
Treatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 110 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | http://www.jeffcopublicschools.org/

## 11 JCS ODL
Facility: Jefferson County Public School Mt. Evans OELS
TYPE OF PERMIT | Domestic-Minor Municipal, lagoon
Permit Number: | CO-0032514
Permit Issue Date | 5/27/2004
Permit Expire Date | 1/31/2009 – Administrative extension
Facility Location: | SW1/4, SW 1/4 of Section4; Township 5 South; Range 72 West; Sixth Principal Meridian. The site is located 8.8 miles west of Evergreen, along Upper Bear Creek Road in Haystack Canyon. Latitude: 39° 38.50’. Longitude: 105° 27.50”
SIC Code: | 4952
Facility Classification: | Class C
Facility Hydraulic Capacity: | 7,500gpd
Facility Organic Capacity: | 78.7 lbs. /day
Treatment Works: | The present wastewater facility consists of septic tank pretreatment, a lined 97,000 gallons aeration pond and two 400,000 gallon unlined evaporation/ infiltration ponds.
Lift Stations: | None
Service Areas: | Jefferson County Public School Mt. Evans OELS
Compliance Schedules | Repairs from 2013 flooding event
Industrial Pretreatment Program | None
2013 Service Area Population Estimate: | 8 (125 EQR). School, 100 students +25 staff (Year-round)
2035 Service Area Population Estimate: | No expected increase in EQRs
2013 Average Daily Effluent Treated: | 2,000 gpd
Plant Expansion: | None
Discharge Point: | MW 050B and MW 050C
Waterbody Identification: | Haystack Creek alluvium
Receiving Water Designation (Segment): | 3. All tributaries to Bear Creek, including all wetlands, from the source to the outlet of Evergreen Lake
Receiving Water Classification (Segment): | Aq. Life Cold 1, Recreation E, Water Supply, Agriculture
Threatened and Endangered Species | None
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 20 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | http://www.jeffcopublicschools.org/

## 12 Fort
Facility:
TYPE OF PERMIT | Domestic- Minor Municipal, Mechanical Plant
Permit Number:
Permit Issue Date
Permit Expire Date
Facility Location:
SIC Code:
Facility Classification:
Facility Hydraulic Capacity:
Facility Organic Capacity:
Treatment Works:
Lift Stations:
Service Areas:
Compliance Schedules
Industrial Pretreatment Program
2014 Service Area Population Estimate: | 1 EQR, Resturant, 300+ seats, Special Events
2035 Service Area Population Estimate:
2014 Average Daily Effluent Treated:
Plant Expansion:
Discharge Point:
Waterbody Identification:
Receiving Water Designation (Segment):
Receiving Water Classification (Segment):
Treatened and Endangered Species
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 18 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch, Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site | http://thefort.com/

## Tiny Town
Facility:
TYPE OF PERMIT | Domestic- Minor Municipal, Mechanical Plant
Permit Number:
Permit Issue Date
Permit Expire Date
Facility Location:
SIC Code:
Facility Classification:
Facility Hydraulic Capacity:
Facility Organic Capacity:
Treatment Works:
Lift Stations:
Service Areas:
Compliance Schedules
Industrial Pretreatment Program
2014 Service Area Population Estimate: | 1 EQR, Business, Summer Tourist, 100 Transients/day
2035 Service Area Population Estimate:
2014 Average Daily Effluent Treated:
Plant Expansion:
Discharge Point:
Waterbody Identification:
Receiving Water Designation (Segment):
Receiving Water Classification (Segment):
Threatened and Endangered Species
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | None
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site

## Geneva Glen
Facility:
TYPE OF PERMIT | Domestic- Minor Municipal, Mechanical Plant
Permit Number:
Permit Issue Date
Permit Expire Date
Facility Location:
SIC Code:
Facility Classification:
Facility Hydraulic Capacity:
Facility Organic Capacity:
Treatment Works:
Lift Stations:
Service Areas:
Compliance Schedules
Industrial Pretreatment Program
2014 Service Area Population Estimate: | 3 EQRs, School/Camp, 28 beds students + 12 staff (year-round, primarily summer
2035 Service Area Population Estimate:
2014 Average Daily Effluent Treated:
Plant Expansion:
Discharge Point:
Waterbody Identification:
Receiving Water Designation (Segment):
Receiving Water Classification (Segment):
Treatened and Endangered Species
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation | Cumulative annual limitation is 5 pounds of total phosphorus
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | Aquatic life and temperature
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site

## BCC
Facility:
TYPE OF PERMIT
Permit Number:
Permit Issue Date
Permit Expire Date
Facility Location:
SIC Code:
Facility Classification:
Facility Hydraulic Capacity:
Facility Organic Capacity:
Treatment Works:
Lift Stations:
Service Areas:
Compliance Schedules
Industrial Pretreatment Program
2014 Service Area Population Estimate: | 9 EQRs, Hotel, 8 cabins and 1 home
2035 Service Area Population Estimate:
2014 Average Daily Effluent Treated:
Plant Expansion:
Discharge Point:
Waterbody Identification:
Receiving Water Designation (Segment):
Receiving Water Classification (Segment):
Treatened and Endangered Species
Control Regulation #74 | Because the discharge from this facility ultimately impacts Bear Creek Reservoir, it is subject to the Bear Creek Control Regulation, Regulation 74. This regulation imposes a total phosphorus concentration limitation of 1.0 mg/l on all dischargers in the watershed. In addition, the regulation specifies a mass limitation for dischargers of record.
Control Regulation #74 Wasteload Allocation
Control Regulation #74 Total Phosphorus Limit | 1.0 mg/l as monthly average
303(d) Listing Regulation #93 | Aquatic life and temperature
Temporary Modifications | None
Water Quality Pollutants of Concern | phosphorus, nitrogen, temperature, ammonia
Water Quality Assessment | WQCD 9-11-2012 completed for Bear Creek, Troublesome Gulch,Mount Vernon Creek, and an unnamed tributary to Bear Creek, near the Evergreen Metropolitan District Wastewater Treatment Facility (WWTF), Bear Creek Cabins WWTF, Kittredge Sanitation and Water District (S&WD) WWTF, West Jefferson County Metro District WWTF, Genesee Water and Sanitation District WWTF, the Forest Hills Metropolitan District WWTF, and the Town of Morrison WWTF.
BCWA Factsheets | BCWA Factsheet 26 BCW Demographics, BCWA Factsheet 41 Wastewater Demographics
Web Site

## Reg 85 Costs
cost per set with filtration = $100 |  | 2013
Evergreen | 5 | 500
West Jeff. | 5 | 500
Kittredge | 5 | 500
Genesee | 5 | 500
Forest Hills | 5 | 500
Conifer Sanitation | 4 | 400

## Regulation 85 2013
WWTF | Parameter | Method | MDL | PQL |  | 2013-03-28 | 2013-05-23 | 2013-07-25 | 2013-09-26 | 2013-11-25
Evergreen | Total Nitrogen | QuikChem 10-107-04-4-B | 6 | 42 | µg/L | 12421 | 6513 | 5382 | 5355 | 8464
| Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-B | 2 | 14 | µg/L | 10427 | 5433 | 4513 | 3588 | 6824
| Nitrogen, ammonia | QuikChem 10-107-06-3-D | 3 | 21 | µg/L | 32 | 49 | 37 | 217 | 130
| Phosphorus, total | QuikChem 10-115-01-4-B | 2 | 14 | µg/L | 103 | 158 | 479 | 67 | 178
West Jeff. | Total Nitrogen | QuikChem 10-107-04-4-B | 6 | 42 | µg/L | 3104 | 2554 | 2532 | 5288 | 5801
| Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-B | 2 | 14 | µg/L | 1781 | 1062 | 999 | 2770 | 1055
| Nitrogen, ammonia | QuikChem 10-107-06-3-D | 3 | 21 | µg/L | 29 | 385 | 173 | 745 | 3294
| Phosphorus, total | QuikChem 10-115-01-4-B | 2 | 14 | µg/L | 106 | 134 | 147 | 116 | 225
Kittredge | Total Nitrogen | QuikChem 10-107-04-4-B | 6 | 42 | µg/L | 22097 | 13393 | 22973 | 11867 | 20678
| Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-B | 2 | 14 | µg/L | 17003 | 11980 | 19058 | 7568 | 17195
| Nitrogen, ammonia | QuikChem 10-107-06-3-D | 3 | 21 | µg/L | 311 | 143 | 1887 | 995 | 1243
| Phosphorus, total | QuikChem 10-115-01-4-B | 2 | 14 | µg/L | 616 | 517 | 473 | 340 | 364
Genesee | Total Nitrogen | QuikChem 10-107-04-4-B | 6 | 42 | µg/L | 7279 | 7615 | 8491 | 13758 | 7137
| Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-B | 2 | 14 | µg/L | 5374 | 6781 | 4179 | 6616 | 6765
| Nitrogen, ammonia | QuikChem 10-107-06-3-D | 3 | 21 | µg/L | 66 | 115 | 219 | 50 | 106
| Phosphorus, total | QuikChem 10-115-01-4-B | 2 | 14 | µg/L | 246 | 213 | 272 | 218 | 206
Forest Hills | Total Nitrogen | QuikChem 10-107-04-4-B | 6 | 42 | µg/L | 13045 | 6642 | 7605 | 25009 | 30193
| Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-B | 2 | 14 | µg/L | 5828 | 4911 | 5959 | 16539 | 25392
| Nitrogen, ammonia | QuikChem 10-107-06-3-D | 3 | 21 | µg/L | 56 | 414 | 63 | 168 | 228
| Phosphorus, total | QuikChem 10-115-01-4-B | 2 | 14 | µg/L | 2579 | 190 | 120 | 405 | 502
Conifer Sanitation | Total Nitrogen | QuikChem 10-107-04-4-B | 6 | 42 | µg/L | NF | 1402 | 5093 | 2117 | 2035
| Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-B | 2 | 14 | µg/L | NF | 815 | 1972 | 1093 | 1242
| Nitrogen, ammonia | QuikChem 10-107-06-3-D | 3 | 21 | µg/L | NF | 29 | 440 | 114 | 75
| Phosphorus, total | QuikChem 10-115-01-4-B | 2 | 14 | µg/L | NF | 31 | 687 | 44 | 59
JCS High School | Total Nitrogen | QuikChem 10-107-04-4-B | 6 | 42 | µg/L | 13663
| Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-B | 2 | 14 | µg/L | 13418
| Nitrogen, ammonia | QuikChem 10-107-06-3-D | 3 | 21 | µg/L | 6
| Phosphorus, total | QuikChem 10-115-01-4-B | 2 | 14 | µg/L | 2
Effluent Monitoring
Parameter | Practical Quantitation Limits
Ammonia | 1 mg/l
N-Ammonia | 50 μg/l
N Nitrate/Nitrite | 0.5 mg/l
N-Nitrate | 50 μg/l
N-Nitrite | 10 μg/l
Total Nitrogen | 0.5 mg/l
Phosphorus | 10 μg/l
Total Kjeldahl Nitrogen | 0.5 mg/l

## Regulation 85 2014
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE | WWTF | Parameter | Method | MDL | PQL | unit | 2014-01-09 | 2014-03-13 | 2014-05-08 | 2014-07-10 | 2014-09-11 | 2014-11-13 |  | 2014 Wastwater Flow Daily Average MGD
BC114C-1 | EMD WWTP | 2014-01-09 | 2014-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 5589 | 5589 |  | µg/L | 6 | 42 | 2014-01-14 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 5589 | 8593 | 4177 | 13633 | 9020 | 11269 |  | BCWA 20 | BCWA 21 | BCWA 22 | BCWA 23 | BCWA 34A | BCWA 73 | BCWA 59
BC114C-1 | EMD WWTP | 2014-01-09 | 2014-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4237 | 4237 |  | µg/L | 2 | 8 | 2014-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 4237 | 3881 | 3003 | 5316 | 7278 | 9050 | JAN | 0.43009 | 0.45588 | 0.05 | 0.23 | 0.017322 | 0.0036 | 0.009
BC114C-1 | EMD WWTP | 2014-01-09 | 2014-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 947 | 947 |  | µg/L | 5 | 35 | 2014-01-28 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 947 | 3610 | 323 | 7274 | 307 | 152 | FEB | 0.43 | 0.42476 | 0.05 | 0.23 | 0.017448 | 0.0035 | 0.006
BC114C-1 | EMD WWTP | 2014-01-09 | 2014-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 70 | 70 |  | µg/L | 2 | 8 | 2014-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 70 | 118 | 142 | 319 | 664 | 388 | MAR | 0.45 | 0.4 | 0.07 | 0.22 | 0.02108 | 0.0035 | 0.006
BC114C-2 | WJCMD WWTP | 2014-01-09 | 2014-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 17215 | 1715 |  | µg/L | 6 | 42 | 2014-01-14 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 17215 | 20500 | 4678 | 4991 | 1686 | 6352 | APRIL | 0.43 | 0.41 | 0.06 | 0.23 | 0.01877 | 0.0036 | 0.004
BC114C-2 | WJCMD WWTP | 2014-01-09 | 2014-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 416 | 416 |  | µg/L | 2 | 8 | 2014-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 416 | 226 | 3108 | 2782 | 401 | 2828 | MAY | 0.51 | 0.5 | 0.06 | 0.25 | 0.018885 | 0.0035 | 0.008
BC114C-2 | WJCMD WWTP | 2014-01-09 | 2014-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 15882 | 15882 |  | µg/L | 5 | 35 | 2014-01-28 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 15882 | 21289 | 84 | 373 | 224 | 2299 | JUNE | 0.48 | 0.49 | 0.05 | 0.24 | 0.017262 | 0.0036 | 0.003
BC114C-2 | WJCMD WWTP | 2014-01-09 | 2014-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 670 | 670 |  | µg/L | 2 | 8 | 2014-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 670 | 769 | 202 | 156 | 327 | 101 | JULY | 0.52 | 0.46 | 0.06 | 0.23 | 0.021258 | 0.0036 | None
BC114C-3 | KSWD WWTP | 2014-01-09 | 2014-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 20898 | 20898 |  | µg/L | 6 | 42 | 2014-01-14 | Kittredge WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 20898 | 7029 | 24453 | 8520 | 12539 | 20596 | AUG | 0.51 | 0.48 | 0.06 | 0.22 | 0.019171 | 0.0036 | 0.005
BC114C-3 | KSWD WWTP | 2014-01-09 | 2014-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 18748 | 18748 |  | µg/L | 2 | 8 | 2014-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 18748 | 3106 | 23715 | 5246 | 10640 | 18630 | SEPT | 0.45 | 0.49 | 0.05 | 0.22 | 0.018908 | 0.0035 | 0.003
BC114C-3 | KSWD WWTP | 2014-01-09 | 2014-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 867 | 867 |  | µg/L | 5 | 35 | 2014-01-28 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 867 | 881 | 1022 | 1033 | 386 | 636 | OCT | 0.43 | 0.47 | 0.05 | 0.21 | 0.018353 | 0.0035 | 0.0046
BC114C-3 | KSWD WWTP | 2014-01-09 | 2014-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 340 | 340 |  | µg/L | 2 | 8 | 2014-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 340 | 467 | 717 | 452 | 300 | 283 | NOV | 0.41 | 0.45 | 0.05 | 0.22 | 0.019006 | 0.0036 | 0.0044
BC114C-4 | GWSD WWTP | 2014-01-09 | 2014-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 7238 | 7238 |  | µg/L | 6 | 42 | 2014-01-14 | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 7238 | 6008 | 6010 | 9452 | 14099 | 10095 | DEC | 0.39 | 0.45 | 0.05 | 0.23 | 0.018973 | 0.0034 | 0.0044
BC114C-4 | GWSD WWTP | 2014-01-09 | 2014-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6382 | 6382 |  | µg/L | 2 | 8 | 2014-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 6382 | 3982 | 5271 | 7976 | 8146 | 8096
BC114C-4 | GWSD WWTP | 2014-01-09 | 2014-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 132 | 132 |  | µg/L | 5 | 35 | 2014-01-28 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 132 | 701 | 80 | 107 | 418 | 90
BC114C-4 | GWSD WWTP | 2014-01-09 | 2014-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 472 | 472 |  | µg/L | 2 | 8 | 2014-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 472 | 166 | 123 | 346 | 508 | 174
BC114C-5 | Conifer Metro WWTP | 2014-01-09 | 2014-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 5468 | 5468 |  | µg/L | 6 | 42 | 2014-01-14 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 5468 | 2507 | 2166 | 2124 | 2362 | 2986
BC114C-5 | Conifer Metro WWTP | 2014-01-09 | 2014-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4244 | 4244 |  | µg/L | 2 | 8 | 2014-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 4244 | 1743 | 1513 | 1195 | 1543 | 2321
BC114C-5 | Conifer Metro WWTP | 2014-01-09 | 2014-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 83 | 83 |  | µg/L | 5 | 35 | 2014-01-28 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 83 | 114 | 28 | 35 | 79 | 2
BC114C-5 | Conifer Metro WWTP | 2014-01-09 | 2014-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 286 | 286 |  | µg/L | 2 | 8 | 2014-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 286 | 24 | 101 | 55 | 25 | 35
BC114C-6 | Conifer High School | 2014-01-09 | 2014-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 59547 | 59547 |  | µg/L | 6 | 42 | 2014-01-14 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 59547 | 62571 | 55547 | NS | 59391 | 60348
BC114C-6 | Conifer High School | 2014-01-09 | 2014-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 57888 | 57888 |  | µg/L | 2 | 8 | 2014-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 57888 | 62528 | 58522 | NS | 46000 | 58738
BC114C-6 | Conifer High School | 2014-01-09 | 2014-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 46 | 46 |  | µg/L | 5 | 35 | 2014-01-28 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 46 | 144 | 33 | NS | 66 | 243
BC114C-6 | Conifer High School | 2014-01-09 | 2014-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 162 | 162 |  | µg/L | 2 | 8 | 2014-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 162 | 143 | 326 | NS | 108 | 2
BC114C-7 | Forest Hills WWTP | 2014-01-09 | 2014-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 25077 | 25077 |  | µg/L | 6 | 42 | 2014-01-14 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 25077 | 28667 | 17324 | 15229 | 20683 | 31771
BC114C-7 | Forest Hills WWTP | 2014-01-09 | 2014-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 23775 | 23775 |  | µg/L | 2 | 8 | 2014-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 23775 | 25832 | 19111 | 13079 | 20168 | 26966
BC114C-7 | Forest Hills WWTP | 2014-01-09 | 2014-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 140 | 140 |  | µg/L | 5 | 35 | 2014-01-28 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 140 | 1050 | 20 | 73 | 119 | 175
BC114C-7 | Forest Hills WWTP | 2014-01-09 | 2014-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 395 | 395 |  | µg/L | 2 | 8 | 2014-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 395 | 309 | 412 | 194 | 585 | 271
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE
BC114C-1 | EMD WWTP | 2014-03-13 | 2014-03-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 8593 | 8593 |  | µg/L | 6 | 42 | 2014-03-19 |  | 2014 Monthly Average Discharge Flow in MGD
BC114C-1 | EMD WWTP | 2014-03-13 | 2014-03-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3881 | 3881 |  | µg/L | 2 | 8 | 2014-03-13
BC114C-1 | EMD WWTP | 2014-03-13 | 2014-03-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 3610 | 3610 |  | µg/L | 5 | 35 | 2014-03-28 |  | CONIFER Sr. WWTP | Mt. Evans OELS
BC114C-2 | WJMD WWTP | 2014-03-13 | 2014-03-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 20500 | 20500 |  | µg/L | 6 | 42 | 2014-03-19 | JAN | 0.009 | 0.0008
BC114C-2 | WJMD WWTP | 2014-03-13 | 2014-03-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 226 | 226 |  | µg/L | 2 | 8 | 2014-03-13 | FEB | 0.006 | 0.0012
BC114C-2 | WJMD WWTP | 2014-03-13 | 2014-03-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 21289 | 21289 |  | µg/L | 5 | 35 | 2014-03-28 | MAR | 0.006 | 0.001
BC114C-2 | WJMD WWTP | 2014-03-13 | 2014-03-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 769 | 769 |  | µg/L | 2 | 8 | 2014-03-19 | APR | 0.004 | 0.001
BC114C-3 | KSWD WWTP | 2014-03-13 | 2014-03-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 7029 | 7029 |  | µg/L | 6 | 42 | 2014-03-19 | MAY | 0.008 | 0.0006
BC114C-3 | KSWD WWTP | 2014-03-13 | 2014-03-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3106 | 3106 |  | µg/L | 2 | 8 | 2014-03-13 | JUN | 0.003 | 0.0002
BC114C-3 | KSWD WWTP | 2014-03-13 | 2014-03-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 881 | 881 |  | µg/L | 5 | 35 | 2014-03-28 | JUL | No Discharge | 0.0002
BC114C-3 | KSWD WWTP | 2014-03-13 | 2014-03-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 467 | 467 |  | µg/L | 2 | 8 | 2014-03-19 | AUG | 0.005 | 0.0007
BC114C-4 | GWSD WWTP | 2014-03-13 | 2014-03-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 6008 | 6008 |  | µg/L | 6 | 42 | 2014-03-19 | SEP | 0.003 | 0.001
BC114C-4 | GWSD WWTP | 2014-03-13 | 2014-03-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3982 | 3982 |  | µg/L | 2 | 8 | 2014-03-13 | OCT | 0.0046 | 0.0015
BC114C-4 | GWSD WWTP | 2014-03-13 | 2014-03-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 701 | 701 |  | µg/L | 5 | 35 | 2014-03-28 | NOV | 0.0044 | 0.0011
BC114C-4 | GWSD WWTP | 2014-03-13 | 2014-03-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 166 | 166 |  | µg/L | 2 | 8 | 2014-03-19 | DEC | 0.0044 | 0.0008
| Conifer Metro WWTP | 2014-03-13 | 2014-03-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 2507 | 2507 |  | µg/L | 6 | 42 | 2014-03-19
| Conifer Metro WWTP | 2014-03-13 | 2014-03-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1743 | 1743 |  | µg/L | 2 | 8 | 2014-03-13
| Conifer Metro WWTP | 2014-03-13 | 2014-03-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 114 | 114 |  | µg/L | 5 | 35 | 2014-03-28 |  | Month | Average Flow | P Concentration | P Loading | Days | Subtotal
| Conifer Metro WWTP | 2014-03-13 | 2014-03-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 24 | 24 |  | µg/L | 2 | 8 | 2014-03-19 |  |  | [MGD] | [mg/L] | [pounds/day] |  | [pounds]
BC114C-5 | Conifer High School | 2014-03-13 | 2014-03-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 62571 | 62571 |  | µg/L | 6 | 42 | 2014-03-19 |  | January | 0.017322 | 0.26 | 0.037561 | 31 | 1.1644
BC114C-5 | Conifer High School | 2014-03-13 | 2014-03-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 62528 | 62528 |  | µg/L | 2 | 8 | 2014-03-13 |  | February | 0.017448 | 0.24 | 0.034924 | 28 | 0.97787
BC114C-5 | Conifer High School | 2014-03-13 | 2014-03-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 144 | 144 |  | µg/L | 5 | 35 | 2014-03-28 |  | March | 0.02108 | 0.4 | 0.070323 | 31 | 2.18
BC114C-5 | Conifer High School | 2014-03-13 | 2014-03-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 143 | 143 |  | µg/L | 2 | 8 | 2014-03-19 |  | April | 0.01877 | 0.15 | 0.023481 | 30 | 0.70444
BC114C-6 | Forest Hills WWTP | 2014-03-13 | 2014-03-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 28667 | 28667 |  | µg/L | 6 | 42 | 2014-03-19 |  | May | 0.018885 | 0.95 | 0.14963 | 31 | 4.6384
BC114C-6 | Forest Hills WWTP | 2014-03-13 | 2014-03-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 25832 | 25832 |  | µg/L | 2 | 8 | 2014-03-13 |  | June | 0.017262 | 0.44 | 0.063345 | 30 | 1.9003
BC114C-6 | Forest Hills WWTP | 2014-03-13 | 2014-03-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1050 | 1050 |  | µg/L | 5 | 35 | 2014-03-28 |  | July | 0.021258 | 0.26 | 0.046096 | 31 | 1.429
BC114C-6 | Forest Hills WWTP | 2014-03-13 | 2014-03-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 309 | 309 |  | µg/L | 2 | 8 | 2014-03-19 |  | August | 0.019171 | 0.41 | 0.065553 | 31 | 2.0322
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE |  | September | 0.018908 | 0.52 | 0.082 | 30 | 2.46
BC514-1 | EMD WWTP | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 4177 | 4177 |  | µg/L | 6 | 42 | 2014-05-13 |  | October | 0.018353 | 0.63 | 0.09643 | 31 | 2.9893
BC514-1 | EMD WWTP | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3003 | 3003 |  | µg/L | 2 | 8 | 2014-05-09 |  | November | 0.019006 | 0.45 | 0.07133 | 30 | 2.1399
BC514-1 | EMD WWTP | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 323 | 323 |  | µg/L | 5 | 35 | 2014-05-14 |  | December | 0.018973 | 0.19 | 0.030065 | 31 | 0.932
BC514-1 | EMD WWTP | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 142 | 142 |  | µg/L | 2 | 8 | 2014-05-13 | [5 empty] | Total | 23.5478
BC514-2 | WJMD WWTP | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 4678 | 4678 |  | µg/L | 6 | 42 | 2014-05-13
BC514-2 | WJMD WWTP | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3108 | 3108 |  | µg/L | 2 | 8 | 2014-05-09
BC514-2 | WJMD WWTP | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 84 | 84 |  | µg/L | 5 | 35 | 2014-05-14 | WWTF | Parameter | Method | MDL | PQL | unit | 2014-01-09 | 2014-03-13 | 2014-05-08 | 2014-07-10 | 2014-09-11 | 2014-11-13
BC514-2 | WJMD WWTP | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 202 | 202 |  | µg/L | 2 | 8 | 2014-05-13 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | mg/L | 5.589 | 8.593 | 4.177 | 13.633 | 9.02 | 11.269
BC514-3 | KSWD WWTP | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 24453 | 24453 |  | µg/L | 6 | 42 | 2014-05-13 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | mg/L | 4.237 | 3.881 | 3.003 | 5.316 | 7.278 | 9.05
BC514-3 | KSWD WWTP | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 23715 | 23715 |  | µg/L | 2 | 8 | 2014-05-09 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | mg/L | 0.947 | 3.61 | 0.323 | 7.274 | 0.307 | 0.152
BC514-3 | KSWD WWTP | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1022 | 1022 |  | µg/L | 5 | 35 | 2014-05-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | mg/L | 0.07 | 0.118 | 0.142 | 0.319 | 0.664 | 0.388
BC514-3 | KSWD WWTP | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 717 | 717 |  | µg/L | 2 | 8 | 2014-05-13 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | mg/L | 17.215 | 20.5 | 4.678 | 4.991 | 1.686 | 6.352
BC514-4 | GWSD WWTP | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 6010 | 6010 |  | µg/L | 6 | 42 | 2014-05-13 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | mg/L | 0.416 | 0.226 | 3.108 | 2.782 | 0.401 | 2.828
BC514-4 | GWSD WWTP | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5271 | 5271 |  | µg/L | 2 | 8 | 2014-05-09 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | mg/L | 15.882 | 21.289 | 0.084 | 0.373 | 0.224 | 2.299
BC514-4 | GWSD WWTP | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 80 | 80 |  | µg/L | 5 | 35 | 2014-05-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | mg/L | 0.67 | 0.769 | 0.202 | 0.156 | 0.327 | 0.101
BC514-4 | GWSD WWTP | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 123 | 123 |  | µg/L | 2 | 8 | 2014-05-13 | Kittredge WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | mg/L | 20.898 | 7.029 | 24.453 | 8.52 | 12.539 | 20.596
BC514-5 | Conifer Metro WWTP | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 2166 | 2166 |  | µg/L | 6 | 42 | 2014-05-13 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | mg/L | 18.748 | 3.106 | 23.715 | 5.246 | 10.64 | 18.63
BC514-5 | Conifer Metro WWTP | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1513 | 1513 |  | µg/L | 2 | 8 | 2014-05-09 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | mg/L | 0.867 | 0.881 | 1.022 | 1.033 | 0.386 | 0.636
BC514-5 | Conifer Metro WWTP | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 28 | 28 | J | µg/L | 5 | 35 | 2014-05-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | mg/L | 0.34 | 0.467 | 0.717 | 0.452 | 0.3 | 0.283
BC514-5 | Conifer Metro WWTP | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 101 | 101 |  | µg/L | 2 | 8 | 2014-05-13 | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | mg/L | 7.238 | 6.008 | 6.01 | 9.452 | 14.099 | 10.095
BC514-6 | Conifer High School | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 55547 | 55547 |  | µg/L | 6 | 42 | 2014-05-13 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | mg/L | 6.382 | 3.982 | 5.271 | 7.976 | 8.146 | 8.096
BC514-6 | Conifer High School | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 58522 | 58522 |  | µg/L | 2 | 8 | 2014-05-09 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | mg/L | 0.132 | 0.701 | 0.08 | 0.107 | 0.418 | 0.09
BC514-6 | Conifer High School | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 33 | 33 | J | µg/L | 5 | 35 | 2014-05-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | mg/L | 0.472 | 0.166 | 0.123 | 0.346 | 0.508 | 0.174
BC514-6 | Conifer High School | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 326 | 326 |  | µg/L | 2 | 8 | 2014-05-13 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | mg/L | 5.468 | 2.507 | 2.166 | 2.124 | 2.362 | 2.986
BC514-7 | Forest Hills WWTP | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 17324 | 17324 |  | µg/L | 6 | 42 | 2014-05-13 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | mg/L | 4.244 | 1.743 | 1.513 | 1.195 | 1.543 | 2.321
BC514-7 | Forest Hills WWTP | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 19111 | 19111 |  | µg/L | 2 | 8 | 2014-05-09 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | mg/L | 0.083 | 0.114 | 0.028 | 0.035 | 0.079 | 0.002
BC514-7 | Forest Hills WWTP | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 20 | 20 | J | µg/L | 5 | 35 | 2014-05-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | mg/L | 0.286 | 0.024 | 0.101 | 0.055 | 0.025 | 0.035
BC514-7 | Forest Hills WWTP | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 412 | 412 |  | µg/L | 2 | 8 | 2014-05-13 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | mg/L | 59.547 | 62.571 | 55.547 | NS | 59.391 | 60.348
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | mg/L | 57.888 | 62.528 | 58.522 | NS | 46 | 58.738
BC714B-1 | Evergreen WWTF | 2014-07-10 | 2014-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 13633 | 13633 |  | µg/L | 6 | 42 | 2014-07-24 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | mg/L | 0.046 | 0.144 | 0.033 | NS | 0.066 | 0.243
BC714B-1 | Evergreen WWTF | 2014-07-10 | 2014-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5316 | 5316 |  | µg/L | 2 | 8 | 2014-07-11 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | mg/L | 0.162 | 0.143 | 0.326 | NS | 0.108 | 0.002
BC714B-1 | Evergreen WWTF | 2014-07-10 | 2014-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 7274 | 7274 |  | µg/L | 5 | 35 | 2014-07-16 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | mg/L | 25.077 | 28.667 | 17.324 | 15.229 | 20.683 | 31.771
BC714B-1 | Evergreen WWTF | 2014-07-10 | 2014-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 319 | 319 |  | µg/L | 2 | 8 | 2014-07-24 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | mg/L | 23.775 | 25.832 | 19.111 | 13.079 | 20.168 | 26.966
BC714B-2 | West Jeff WWTF | 2014-07-10 | 2014-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 4991 | 4991 |  | µg/L | 6 | 42 | 2014-07-24 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | mg/L | 0.14 | 1.05 | 0.02 | 0.073 | 0.119 | 0.175
BC714B-2 | West Jeff WWTF | 2014-07-10 | 2014-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2782 | 2782 |  | µg/L | 2 | 8 | 2014-07-11 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | mg/L | 0.395 | 0.309 | 0.412 | 0.194 | 0.585 | 0.271
BC714B-2 | West Jeff WWTF | 2014-07-10 | 2014-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 373 | 373 |  | µg/L | 5 | 35 | 2014-07-16
BC714B-2 | West Jeff WWTF | 2014-07-10 | 2014-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 156 | 156 |  | µg/L | 2 | 8 | 2014-07-24
BC714B-3 | Kittredge WWTF | 2014-07-10 | 2014-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 8520 | 8520 |  | µg/L | 6 | 42 | 2014-07-24
BC714B-3 | Kittredge WWTF | 2014-07-10 | 2014-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5246 | 5246 |  | µg/L | 2 | 8 | 2014-07-11
BC714B-3 | Kittredge WWTF | 2014-07-10 | 2014-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1033 | 1033 |  | µg/L | 5 | 35 | 2014-07-16
BC714B-3 | Kittredge WWTF | 2014-07-10 | 2014-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 452 | 452 |  | µg/L | 2 | 8 | 2014-07-24
BC714B-4 | Genesee WWTF | 2014-07-10 | 2014-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 9452 | 9452 |  | µg/L | 6 | 42 | 2014-07-24
BC714B-4 | Genesee WWTF | 2014-07-10 | 2014-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7976 | 7976 |  | µg/L | 2 | 8 | 2014-07-11
BC714B-4 | Genesee WWTF | 2014-07-10 | 2014-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 107 | 107 |  | µg/L | 5 | 35 | 2014-07-16
BC714B-4 | Genesee WWTF | 2014-07-10 | 2014-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 346 | 346 |  | µg/L | 2 | 8 | 2014-07-24
| Conifer Metro WWTF | 2014-07-10 | 2014-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 2124 | 2124 |  | µg/L | 6 | 42 | 2014-07-24
| Conifer Metro WWTF | 2014-07-10 | 2014-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1195 | 1195 |  | µg/L | 2 | 8 | 2014-07-11
| Conifer Metro WWTF | 2014-07-10 | 2014-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 35 | 35 | J | µg/L | 5 | 35 | 2014-07-16
| Conifer Metro WWTF | 2014-07-10 | 2014-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 55 | 55 |  | µg/L | 2 | 8 | 2014-07-24
BC714B-5 | Conifer High School | 2014-05-08 | 2014-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | NS
BC714B-5 | Conifer High School | 2014-05-08 | 2014-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | NS
BC714B-5 | Conifer High School | 2014-05-08 | 2014-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | NS
BC714B-5 | Conifer High School | 2014-05-08 | 2014-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | NS
BC714B-6 | Forest Hills WWTF | 2014-07-10 | 2014-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 15229 | 15229 |  | µg/L | 6 | 42 | 2014-07-24
BC714B-6 | Forest Hills WWTF | 2014-07-10 | 2014-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 13079 | 13079 |  | µg/L | 2 | 8 | 2014-07-11
BC714B-6 | Forest Hills WWTF | 2014-07-10 | 2014-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 73 | 73 |  | µg/L | 5 | 35 | 2014-07-16
BC714B-6 | Forest Hills WWTF | 2014-07-10 | 2014-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 194 | 194 |  | µg/L | 2 | 8 | 2014-07-24
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE
BC914B-1 | EMD WWTF | 2014-09-11 | 2014-09-11 | Total Nitrogen | SW | QC 10-107-04-4-B | 9020 | 9020 |  | µg/L | 6 | 42 | 2014-09-30
BC914B-1 | EMD WWTF | 2014-09-11 | 2014-09-11 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7278 | 7278 |  | µg/L | 2 | 8 | 2014-09-22
BC914B-1 | EMD WWTF | 2014-09-11 | 2014-09-11 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 307 | 307 |  | µg/L | 5 | 35 | 2014-09-18
BC914B-1 | EMD WWTF | 2014-09-11 | 2014-09-11 | Phosphorus, total | SW | QC 10-115-01-4-B | 664 | 664 |  | µg/L | 2 | 8 | 2014-09-30
BC914B-2 | WJCMD WWTF | 2014-09-11 | 2014-09-11 | Total Nitrogen | SW | QC 10-107-04-4-B | 1686 | 1686 |  | µg/L | 6 | 42 | 2014-09-30
BC914B-2 | WJCMD WWTF | 2014-09-11 | 2014-09-11 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 401 | 401 |  | µg/L | 2 | 8 | 2014-09-22
BC914B-2 | WJCMD WWTF | 2014-09-11 | 2014-09-11 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 224 | 224 |  | µg/L | 5 | 35 | 2014-09-18
BC914B-2 | WJCMD WWTF | 2014-09-11 | 2014-09-11 | Phosphorus, total | SW | QC 10-115-01-4-B | 327 | 327 |  | µg/L | 2 | 8 | 2014-09-30
BC914B-3 | KSWD WWTF | 2014-09-11 | 2014-09-11 | Total Nitrogen | SW | QC 10-107-04-4-B | 12539 | 12539 |  | µg/L | 6 | 42 | 2014-09-30
BC914B-3 | KSWD WWTF | 2014-09-11 | 2014-09-11 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 10640 | 10640 |  | µg/L | 2 | 8 | 2014-09-22
BC914B-3 | KSWD WWTF | 2014-09-11 | 2014-09-11 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 386 | 386 |  | µg/L | 5 | 35 | 2014-09-18
BC914B-3 | KSWD WWTF | 2014-09-11 | 2014-09-11 | Phosphorus, total | SW | QC 10-115-01-4-B | 300 | 300 |  | µg/L | 2 | 8 | 2014-09-30
BC914B-4 | GWSD WWTF | 2014-09-11 | 2014-09-11 | Total Nitrogen | SW | QC 10-107-04-4-B | 14099 | 14099 |  | µg/L | 6 | 42 | 2014-09-30
BC914B-4 | GWSD WWTF | 2014-09-11 | 2014-09-11 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 8146 | 8146 |  | µg/L | 2 | 8 | 2014-09-22
BC914B-4 | GWSD WWTF | 2014-09-11 | 2014-09-11 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 418 | 418 |  | µg/L | 5 | 35 | 2014-09-18
BC914B-4 | GWSD WWTF | 2014-09-11 | 2014-09-11 | Phosphorus, total | SW | QC 10-115-01-4-B | 508 | 508 |  | µg/L | 2 | 8 | 2014-09-30
BC914B-5 | Conifer Metro WWTF | 2014-09-11 | 2014-09-11 | Total Nitrogen | SW | QC 10-107-04-4-B | 2362 | 2362 |  | µg/L | 6 | 42 | 2014-09-30
BC914B-5 | Conifer Metro WWTF | 2014-09-11 | 2014-09-11 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1543 | 1543 |  | µg/L | 2 | 8 | 2014-09-22
BC914B-5 | Conifer Metro WWTF | 2014-09-11 | 2014-09-11 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 79 | 79 |  | µg/L | 5 | 35 | 2014-09-18
BC914B-5 | Conifer Metro WWTF | 2014-09-11 | 2014-09-11 | Phosphorus, total | SW | QC 10-115-01-4-B | 25 | 25 |  | µg/L | 2 | 8 | 2014-09-30
BC914B-6 | Jeffco. Public Schools Conifer | 2014-09-11 | 2014-09-11 | Total Nitrogen | SW | QC 10-107-04-4-B | 59391 | 59391 |  | µg/L | 6 | 42 | 2014-10-03
BC914B-6 | Jeffco. Public Schools Conifer | 2014-09-11 | 2014-09-11 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 46000 | 46000 |  | µg/L | 2 | 8 | 2014-09-22
BC914B-6 | Jeffco. Public Schools Conifer | 2014-09-11 | 2014-09-11 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 66 | 66 |  | µg/L | 5 | 35 | 2014-09-18
BC914B-6 | Jeffco. Public Schools Conifer | 2014-09-11 | 2014-09-11 | Phosphorus, total | SW | QC 10-115-01-4-B | 108 | 108 |  | µg/L | 2 | 8 | 2014-09-30
BC914B-7 | Forest Hills WWTF | 2014-09-11 | 2014-09-11 | Total Nitrogen | SW | QC 10-107-04-4-B | 20683 | 20683 |  | µg/L | 6 | 42 | 2014-09-30
BC914B-7 | Forest Hills WWTF | 2014-09-11 | 2014-09-11 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 20168 | 20168 |  | µg/L | 2 | 8 | 2014-09-22
BC914B-7 | Forest Hills WWTF | 2014-09-11 | 2014-09-11 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 119 | 119 |  | µg/L | 5 | 35 | 2014-09-18
BC914B-7 | Forest Hills WWTF | 2014-09-11 | 2014-09-11 | Phosphorus, total | SW | QC 10-115-01-4-B | 585 | 585 |  | µg/L | 2 | 8 | 2014-09-30
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE
BC1114-1 | EMD WWTF | 2014-11-13 | 2014-11-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 11269 | 11269 |  | µg/L | 6 | 42 | 2014-12-04
BC1114-1 | EMD WWTF | 2014-11-13 | 2014-11-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9050 | 9050 |  | µg/L | 2 | 8 | 2014-12-03
BC1114-1 | EMD WWTF | 2014-11-13 | 2014-11-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 152 | 152 |  | µg/L | 5 | 35 | 2014-12-08
BC1114-1 | EMD WWTF | 2014-11-13 | 2014-11-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 388 | 388 |  | µg/L | 2 | 8 | 2014-12-04
BC1114-2 | WJCMD WWTF | 2014-11-13 | 2014-11-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 6352 | 6352 |  | µg/L | 6 | 42 | 2014-12-04
BC1114-2 | WJCMD WWTF | 2014-11-13 | 2014-11-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2828 | 2828 |  | µg/L | 2 | 8 | 2014-12-03
BC1114-2 | WJCMD WWTF | 2014-11-13 | 2014-11-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2299 | 2299 |  | µg/L | 5 | 35 | 2014-12-08
BC1114-2 | WJCMD WWTF | 2014-11-13 | 2014-11-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 101 | 101 |  | µg/L | 2 | 8 | 2014-12-04
BC1114-3 | KSWD WWTF | 2014-11-13 | 2014-11-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 20596 | 20596 |  | µg/L | 6 | 42 | 2014-12-04
BC1114-3 | KSWD WWTF | 2014-11-13 | 2014-11-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 18630 | 18630 |  | µg/L | 2 | 8 | 2014-12-03
BC1114-3 | KSWD WWTF | 2014-11-13 | 2014-11-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 636 | 636 |  | µg/L | 5 | 35 | 2014-12-08
BC1114-3 | KSWD WWTF | 2014-11-13 | 2014-11-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 283 | 283 |  | µg/L | 2 | 8 | 2014-12-04
BC1114-4 | GWSD WWTF | 2014-11-13 | 2014-11-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 10095 | 10095 |  | µg/L | 6 | 42 | 2014-12-04
BC1114-4 | GWSD WWTF | 2014-11-13 | 2014-11-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 8096 | 8096 |  | µg/L | 2 | 8 | 2014-12-03
BC1114-4 | GWSD WWTF | 2014-11-13 | 2014-11-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 90 | 90 |  | µg/L | 5 | 35 | 2014-12-08
BC1114-4 | GWSD WWTF | 2014-11-13 | 2014-11-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 174 | 174 |  | µg/L | 2 | 8 | 2014-12-04
BC1114-5 | Conifer Metro WWTF | 2014-11-13 | 2014-11-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 2986 | 2986 |  | µg/L | 6 | 42 | 2014-12-04
BC1114-5 | Conifer Metro WWTF | 2014-11-13 | 2014-11-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2321 | 2321 |  | µg/L | 2 | 8 | 2014-12-03
BC1114-5 | Conifer Metro WWTF | 2014-11-13 | 2014-11-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A |  |  |  | µg/L | 5 | 35 | 2014-12-08
BC1114-5 | Conifer Metro WWTF | 2014-11-13 | 2014-11-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 35 | 35 |  | µg/L | 2 | 8 | 2014-12-04
BC1114-6 | Jeffco. Public Schools Conifer | 2014-11-13 | 2014-11-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 60348 | 60348 |  | µg/L | 6 | 42 | 2014-12-04
BC1114-6 | Jeffco. Public Schools Conifer | 2014-11-13 | 2014-11-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 58738 | 58738 |  | µg/L | 2 | 8 | 2014-12-03
BC1114-6 | Jeffco. Public Schools Conifer | 2014-11-13 | 2014-11-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 243 | 243 |  | µg/L | 5 | 35 | 2014-12-08
BC1114-6 | Jeffco. Public Schools Conifer | 2014-11-13 | 2014-11-13 | Phosphorus, total | SW | QC 10-115-01-4-B |  |  |  | µg/L | 2 | 8 | 2014-12-04
BC1114-7 | Forest Hills WWTF | 2014-11-13 | 2014-11-13 | Total Nitrogen | SW | QC 10-107-04-4-B | 31771 | 31771 |  | µg/L | 6 | 42 | 2014-12-04
BC1114-7 | Forest Hills WWTF | 2014-11-13 | 2014-11-13 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 26966 | 26966 |  | µg/L | 2 | 8 | 2014-12-03
BC1114-7 | Forest Hills WWTF | 2014-11-13 | 2014-11-13 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 175 | 175 |  | µg/L | 5 | 35 | 2014-12-08
BC1114-7 | Forest Hills WWTF | 2014-11-13 | 2014-11-13 | Phosphorus, total | SW | QC 10-115-01-4-B | 271 | 271 |  | µg/L | 2 | 8 | 2014-12-04

## Regulation 85 2015
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE
BC115B-1 | EMD WWTP | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 10921 | 10921 |  | µg/L | 6 | 42 | 2015-01-14 | WWTF | Parameter | Method | MDL | PQL | unit | 2015-01-08 | 2015-03-12 | 2015-05-14 | 2015-07-09 | 2015-09-10 | 2015-11-12 | WWTF | Parameter | Method | MDL | PQL | unit | 2015-01-08 | 2015-03-12 | 2015-05-14 | 2015-07-09 | 2015-09-10 | 2015-11-12 | TN | NO5 | NH3 | TP
BC115B-1 | EMD WWTP | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7945 | 7945 |  | µg/L | 2 | 8 | 2015-01-08 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 10921 | 10727 | 8616 | 5454 | 6806 | 8427 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 10.921 | 10.727 | 8.616 | 5.454 | 6.806 | 8.427 | 2015-01-14 | 2015-01-08 | 2015-01-09 | 2015-01-14
BC115B-1 | EMD WWTP | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1229 | 1229 |  | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 7945 | 8787 | 4716 | 4513 | 6089 | 7192 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.278 | 0.331 | 0.233 | 0.102 | 0.079 | 0.143 | 2015-03-18 | 2015-03-13 | 2015-03-20 | 2015-03-18
BC115B-1 | EMD WWTP | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 278 | 278 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 1229 | 552 | 397 | 67 | 121 | 556 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 7.945 | 8.787 | 4.716 | 4.513 | 6.089 | 7.192 | 2015-05-21 | 2015-05-14 | 2015-05-20 | 2015-05-21
[27 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 1.229 | 0.552 | 0.397 | 0.067 | 0.121 | 0.556 | 2015-07-16 | 2015-07-14 | 2015-07-10 | 2015-07-16
BC115B-2 | WJCMD WWTP | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 8282 | 8282 |  | µg/L | 6 | 42 | 2015-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 278 | 331 | 233 | 102 | 79 | 143 |  | TIN Calculated |  |  |  |  | 9.174 | 9.339 | 5.113 | 4.58 | 6.21 | 7.748 | 2015-10-08 | 2015-09-15 | 2015-09-11 | 2015-09-25
BC115B-2 | WJCMD WWTP | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3032 | 3032 |  | µg/L | 2 | 8 | 2015-01-08 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 8282 | 8483 | 5482 | 4035 | 7006 | 4206 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 8.282 | 8.483 | 5.482 | 4.035 | 7.006 | 4.206 | 2015-11-25 | 2015-11-13 | 2015-11-13 | 2015-11-25
BC115B-2 | WJCMD WWTP | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 3655 | 3655 |  | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 3032 | 1933 | 2418 | 1368 | 1222 | 2282 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.147 | 0.178 | 0.102 | 0.09 | 1.076 | 0.121
[27 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 3.032 | 1.933 | 2.418 | 1.368 | 1.222 | 2.282
BC115B-2 | WJCMD WWTP | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 147 | 147 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 3655 | 6918 | 1385 | 1271 | 4115 | 508 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 3.655 | 6.918 | 1.385 | 1.271 | 4.115 | 0.508
BC115B-3 | KSWD WWTP | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 14859 | 14859 |  | µg/L | 6 | 42 | 2015-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 147 | 178 | 102 | 90 | 1076 | 121 |  | TIN Calculated |  |  |  |  | 6.687 | 8.851 | 3.803 | 2.639 | 5.337 | 2.79
BC115B-3 | KSWD WWTP | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 11248 | 11248 |  | µg/L | 2 | 8 | 2015-01-08 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 14859 | 9584 | 11383 | 7220 | 11071 | 14434 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 14.859 | 9.584 | 11.383 | 7.22 | 11.071 | 14.434
BC115B-3 | KSWD WWTP | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1259 | 1259 |  | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 11248 | 5652 | 9085 | 5391 | 7752 | 11188 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.439 | 0.261 | 0.113 | 0.297 | 0.632 | 0.343
[27 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 11.248 | 5.652 | 9.085 | 5.391 | 7.752 | 11.188
BC115B-3 | KSWD WWTP | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 439 | 439 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 1259 | 4295 | 362 | 299 | 441 | 433 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 1.259 | 4.295 | 0.362 | 0.299 | 0.441 | 0.433
BC115B-4 | GWSD WWTP | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 9205 | 9205 |  | µg/L | 6 | 42 | 2015-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 439 | 261 | 113 | 297 | 632 | 343 |  | TIN Calculated |  |  |  |  | 12.507 | 9.947 | 9.447 | 5.69 | 8.193 | 11.621
BC115B-4 | GWSD WWTP | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7284 | 7284 |  | µg/L | 2 | 8 | 2015-01-08 | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 9205 | 8794 | 6590 | 10556 | 10255 | 9315 | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 9.205 | 8.794 | 6.59 | 10.556 | 10.255 | 9.315
BC115B-4 | GWSD WWTP | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 86 | 86 |  | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 7284 | 7186 | 4936 | 9111 | 7676 | 7792 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.278 | 0.216 | 0.259 | 0.072 | 0.214 | 0.182
BC115B-4 | GWSD WWTP | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 278 | 278 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 86 | 105 | 63 | 57 | 47 | 55 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 7.284 | 7.186 | 4.936 | 9.111 | 7.676 | 7.792
[27 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.086 | 0.105 | 0.063 | 0.057 | 0.047 | 0.055
BC115B-5 | Conifer Metro WWTP | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1384 | 1384 |  | µg/L | 6 | 42 | 2015-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 278 | 216 | 259 | 72 | 214 | 182 |  | TIN Calculated |  |  |  |  | 7.37 | 7.291 | 4.999 | 9.168 | 7.723 | 7.847
BC115B-5 | Conifer Metro WWTP | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 611 | 611 |  | µg/L | 2 | 8 | 2015-01-08 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 1384 | 71643 | 5901 | 6050 | 8901 | 4239 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 1.384 | 71.643 | 5.901 | 6.05 | 8.901 | 4.239
BC115B-5 | Conifer Metro WWTP | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 51 | 51 |  | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 611 | 67103 | 4024 | 4821 | 30 | 2768 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.017 | 0.039 | 0.012 | 0.058 | 0.093 | 0.219
BC115B-5 | Conifer Metro WWTP | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 17 | 17 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 51 | 34 | 52 | 48 | 8679 | 51 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 0.611 | 67.103 | 4.024 | 4.821 | 0.03 | 2.768
[27 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.051 | 0.034 | 0.052 | 0.048 | 8.679 | 0.051
BC115B-6 | Conifer High School | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 70776 | 70776 |  | µg/L | 6 | 42 | 2015-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 17 | 39 | 12 | 58 | 93 | 219 |  | TIN Calculated |  |  |  |  | 0.662 | 67.137 | 4.076 | 4.869 | 8.709 | 2.819
BC115B-6 | Conifer High School | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 56364 | 56364 |  | µg/L | 2 | 8 | 2015-01-08 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 70776 | 3782 | 44016 | 10654 | 47756 | 58772 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 70.776 | 3.782 | 44.016 | 10.654 | 47.756 | 58.772
BC115B-6 | Conifer High School | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 24 | 24 | J | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 56364 | 2417 | 39217 | 7786 | 51972 | 57697 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.022 | 0.062 | 0.081 | 0.169 | 0.562 | 0.276
BC115B-6 | Conifer High School | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 22 | 22 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 24 | 55 | 29 | 993 | 38 | 22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 56.364 | 2.417 | 39.217 | 7.786 | 51.972 | 57.697
[27 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.024 | 0.055 | 0.029 | 0.993 | 0.038 | 0.022
BC115B-7 | Forest Hills WWTP | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 28430 | 28430 |  | µg/L | 6 | 42 | 2015-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 22 | 62 | 81 | 169 | 562 | 276 |  | TIN Calculated |  |  |  |  | 56.388 | 2.472 | 39.246 | 8.779 | 52.01 | 57.719
BC115B-7 | Forest Hills WWTP | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 24294 | 24294 |  | µg/L | 2 | 8 | 2015-01-08 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 28430 | 20995 | 16413 | 37700 | 27421 | 35599 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 28.43 | 20.995 | 16.413 | 37.7 | 27.421 | 35.599
BC115B-7 | Forest Hills WWTP | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 147 | 147 |  | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 24294 | 18316 | 12750 | 31216 | 21698 | 19875 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.255 | 0.329 | 0.437 | 0.45 | 0.531 | 0.961
BC115B-7 | Forest Hills WWTP | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 255 | 255 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 147 | 1489 | 947 | 86 | 440 | 250 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 24.294 | 18.316 | 12.75 | 31.216 | 21.698 | 19.875
[27 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.147 | 1.489 | 0.947 | 0.086 | 0.44 | 0.25
BC115B-8 | Morrison WWTP | 2015-01-08 | 2015-01-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1484 | 1484 |  | µg/L | 6 | 42 | 2015-01-14 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 255 | 329 | 437 | 450 | 531 | 961 |  | TIN Calculated |  |  |  |  | 24.441 | 19.805 | 13.697 | 31.302 | 22.138 | 20.125
BC115B-8 | Morrison WWTP | 2015-01-08 | 2015-01-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 82 | 82 |  | µg/L | 2 | 8 | 2015-01-08 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 1484 | 7317 | 2432 | 2287 | 2160 | 1474 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 1.484 | 7.317 | 2.432 | 2.287 | 2.16 | 1.474
[27 empty] | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.25 | 0.255 | 0.299 | 0.519 | 1.163 | 0.221
BC115B-8 | Morrison WWTP | 2015-01-08 | 2015-01-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 210 | 210 |  | µg/L | 5 | 35 | 2015-01-09 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 82 | 151 | 199 | 185 | 670 | 52 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 0.082 | 0.151 | 0.199 | 0.185 | 0.67 | 0.052
BC115B-8 | Morrison WWTP | 2015-01-08 | 2015-01-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 250 | 250 |  | µg/L | 2 | 8 | 2015-01-14 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 210 | 6433 | 478 | 410 | 305 | 145 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.21 | 6.433 | 0.478 | 0.41 | 0.305 | 0.145
[15 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 250 | 255 | 299 | 519 | 1163 | 221 |  | TIN Calculated |  |  |  |  | 0.292 | 6.584 | 0.677 | 0.595 | 0.975 | 0.197
BC315-1 | EMD WWTP | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 10727 | 10727 |  | µg/L | 6 | 42 | 2015-03-18
BC315-1 | EMD WWTP | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 8787 | 8787 |  | µg/L | 2 | 8 | 2015-03-13
BC315-1 | EMD WWTP | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 552 | 552 |  | µg/L | 5 | 35 | 2015-03-20
BC315-1 | EMD WWTP | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 331 | 331 |  | µg/L | 2 | 8 | 2015-03-18
BC315-2 | WJCMD WWTP | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 8483 | 8483 |  | µg/L | 6 | 42 | 2015-03-18
BC315-2 | WJCMD WWTP | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1933 | 1933 |  | µg/L | 2 | 8 | 2015-03-13
BC315-2 | WJCMD WWTP | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 6918 | 6918 |  | µg/L | 5 | 35 | 2015-03-20
BC315-2 | WJCMD WWTP | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 178 | 178 |  | µg/L | 2 | 8 | 2015-03-18
BC315-3 | KSWD WWTP | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 9584 | 9584 |  | µg/L | 6 | 42 | 2015-03-18
BC315-3 | KSWD WWTP | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5652 | 5652 |  | µg/L | 2 | 8 | 2015-03-13
BC315-3 | KSWD WWTP | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4295 | 4295 |  | µg/L | 5 | 35 | 2015-03-20
BC315-3 | KSWD WWTP | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 261 | 261 |  | µg/L | 2 | 8 | 2015-03-18
BC315-4 | GWSD WWTP | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 8794 | 8794 |  | µg/L | 6 | 42 | 2015-03-18
BC315-4 | GWSD WWTP | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7186 | 7186 |  | µg/L | 2 | 8 | 2015-03-13
BC315-4 | GWSD WWTP | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 105 | 105 |  | µg/L | 5 | 35 | 2015-03-20
BC315-4 | GWSD WWTP | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 216 | 216 |  | µg/L | 2 | 8 | 2015-03-18
BC315-5 | Conifer Metro WWTP | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 71643 | 71643 |  | µg/L | 6 | 42 | 2015-03-18
BC315-5 | Conifer Metro WWTP | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 67103 | 67103 |  | µg/L | 2 | 8 | 2015-03-13
BC315-5 | Conifer Metro WWTP | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 34 | 34 | J | µg/L | 5 | 35 | 2015-03-20
BC315-5 | Conifer Metro WWTP | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 39 | 39 |  | µg/L | 2 | 8 | 2015-03-18
BC315-6 | Conifer High School | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 3782 | 3782 |  | µg/L | 6 | 42 | 2015-03-18
BC315-6 | Conifer High School | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2417 | 2417 |  | µg/L | 2 | 8 | 2015-03-13
BC315-6 | Conifer High School | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 55 | 55 |  | µg/L | 5 | 35 | 2015-03-20
BC315-6 | Conifer High School | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 62 | 62 |  | µg/L | 2 | 8 | 2015-03-18
BC315-7 | Forest Hills WWTP | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 20995 | 20995 |  | µg/L | 6 | 42 | 2015-03-18
BC315-7 | Forest Hills WWTP | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 18316 | 18316 |  | µg/L | 2 | 8 | 2015-03-13
BC315-7 | Forest Hills WWTP | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1489 | 1489 |  | µg/L | 5 | 35 | 2015-03-20
BC315-7 | Forest Hills WWTP | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 329 | 329 |  | µg/L | 2 | 8 | 2015-03-18
BC315-8 | Morrison WWTP | 2015-03-12 | 2015-03-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 7317 | 7317 |  | µg/L | 6 | 42 | 2015-03-26
BC315-8 | Morrison WWTP | 2015-03-12 | 2015-03-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 151 | 151 |  | µg/L | 2 | 8 | 2015-03-13
BC315-8 | Morrison WWTP | 2015-03-12 | 2015-03-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 6433 | 6433 |  | µg/L | 5 | 35 | 2015-03-20 |  |  | 2015 Flow (MGD)
BC315-8 | Morrison WWTP | 2015-03-12 | 2015-03-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 255 | 255 |  | µg/L | 2 | 8 | 2015-03-18 |  |  | 2015-01-08 | 2015-03-12 | 2015-05-14 | 2015-07-09 | 2015-09-10 | 2015-11-12
[14 empty] | Evergreen Metro District | CO-0031429 | 0.45 | 0.49 | 1.40 | 0.81 | 0.47 | 0.44
BC515-1 | EMD WWTP | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 8616 | 8616 |  | µg/L | 6 | 42 | 2015-05-21 | West Jefferson County Metro District | CO-0020915 | 0.43 | 0 .41 | 0.85 | 0.77 | 0.55 | 0.59
BC515-1 | EMD WWTP | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4716 | 4716 |  | µg/L | 2 | 8 | 2015-05-14 | Kittredge Water and Sanitation District | CO-0023841 | 0.05 | 0.05 | 0.17 | 0.13 | 0.07 | 0.07
BC515-1 | EMD WWTP | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 397 | 397 |  | µg/L | 5 | 35 | 2015-05-20 | Genesee Water and Sanitation District | CO-0022951 | 0.23 | 0.22 | 0.75 | 0.39 | 0.26 | 0.24
BC515-1 | EMD WWTP | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 233 | 233 |  | µg/L | 2 | 8 | 2015-05-21 | Forest Hills Metro District | CO-0037044 | 0.0176 | 0.0189 | 0.0258 | 0.0198 | 0.019303 | 0.019555
BC515-2 | WJCMD WWTP | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 5482 | 5482 |  | µg/L | 6 | 42 | 2015-05-21 | Conifer Metro District | CO-0047295 | 0.012193 | 0.0098 | 0.0246 | 0.0091 | 0.0295 | 0.031152
BC515-2 | WJCMD WWTP | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2418 | 2418 |  | µg/L | 2 | 8 | 2015-05-14 | Conifer Sanitation Association | COX-047392 | 0.0019509 | 0.001568 | 0.003936 | 0.001456 | 0.00472 | 0.0049843 |  |  | 0.0246 | 15.85%
BC515-2 | WJCMD WWTP | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1385 | 1385 |  | µg/L | 5 | 35 | 2015-05-20 | JCS Conifer High School | CO-0047988 | 0.005 | 0.003 | 0.006 | 0.005 | 0.008 | 0.004 |  |  | 0.0039
BC515-2 | WJCMD WWTP | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 102 | 102 |  | µg/L | 2 | 8 | 2015-05-21 | Morrison | CO-0041432 | 0.06 | 0.07 | 0.16 | 0.11 | 0.06 | 0.07
BC515-3 | KSWD WWTP | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 11383 | 11383 |  | µg/L | 6 | 42 | 2015-05-21 | Singing River Ranch | CO-0035971 | 0 | 0 | 0 | 0 | 0 | 0
BC515-3 | KSWD WWTP | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9085 | 9085 |  | µg/L | 2 | 8 | 2015-05-14
BC515-3 | KSWD WWTP | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 362 | 362 |  | µg/L | 5 | 35 | 2015-05-20 |  |  | Time | Sample type
BC515-3 | KSWD WWTP | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 113 | 113 |  | µg/L | 2 | 8 | 2015-05-21 | Evergreen Metro District | CO-0031429 | 9:00 | 12-hr
BC515-4 | GWSD WWTP | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 6590 | 6590 |  | µg/L | 6 | 42 | 2015-05-21 | West Jefferson County Metro District | CO-0020915 | 9:00 | 12-hr
BC515-4 | GWSD WWTP | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4936 | 4936 |  | µg/L | 2 | 8 | 2015-05-14 | Kittredge Water and Sanitation District | CO-0023841 | 9:00 | 12-hr
BC515-4 | GWSD WWTP | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 63 | 63 |  | µg/L | 5 | 35 | 2015-05-20 | Genesee Water and Sanitation District | CO-0022951 | 8:00 | 24-hr
BC515-4 | GWSD WWTP | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 259 | 259 |  | µg/L | 2 | 8 | 2015-05-21 | Forest Hills Metro District | CO-0037044 | 10:00 | 12-hr
BC515-5 | Conifer Metro WWTP | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 5901 | 5901 |  | µg/L | 6 | 42 | 2015-05-21 | Conifer Metro District | CO-047295
BC515-5 | Conifer Metro WWTP | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4024 | 4024 |  | µg/L | 2 | 8 | 2015-05-14 | Conifer Sanitation Association | COX-0047392 | 9:00 | grab
BC515-5 | Conifer Metro WWTP | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 52 | 52 |  | µg/L | 5 | 35 | 2015-05-20 | JCS Conifer High School | CO-047988 | 9:00 | 12-hr
BC515-5 | Conifer Metro WWTP | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 12 | 12 |  | µg/L | 2 | 8 | 2015-05-21 | Morrison | CO-0041432 | 9:00 | 12-hr
BC515-6 | Conifer High School | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 44016 | 44016 |  | µg/L | 6 | 42 | 2015-05-21 | Singing River Ranch | CO-0035971 | na | na
BC515-6 | Conifer High School | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 39217 | 39217 |  | µg/L | 2 | 8 | 2015-05-14
BC515-6 | Conifer High School | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 29 | 29 | J | µg/L | 5 | 35 | 2015-05-20
BC515-6 | Conifer High School | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 81 | 81 |  | µg/L | 2 | 8 | 2015-05-21
BC515-7 | Forest Hills WWTP | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 16413 | 16413 |  | µg/L | 6 | 42 | 2015-05-21
BC515-7 | Forest Hills WWTP | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 12750 | 12750 |  | µg/L | 2 | 8 | 2015-05-14
BC515-7 | Forest Hills WWTP | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 947 | 947 |  | µg/L | 5 | 35 | 2015-05-20
BC515-7 | Forest Hills WWTP | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 437 | 437 |  | µg/L | 2 | 8 | 2015-05-21
BC515-8 | Morrison WWTP | 2015-05-14 | 2015-05-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 2432 | 2432 |  | µg/L | 6 | 42 | 2015-05-21
BC515-8 | Morrison WWTP | 2015-05-14 | 2015-05-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 199 | 199 |  | µg/L | 2 | 8 | 2015-05-14
BC515-8 | Morrison WWTP | 2015-05-14 | 2015-05-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 478 | 478 |  | µg/L | 5 | 35 | 2015-05-20
BC515-8 | Morrison WWTP | 2015-05-14 | 2015-05-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 299 | 299 |  | µg/L | 2 | 8 | 2015-05-21
BC715C-1 | EMD WWTP | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 5454 | 5454 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-1 | EMD WWTP | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4513 | 4513 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-1 | EMD WWTP | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 67 | 67 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-1 | EMD WWTP | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 102 | 102 |  | µg/L | 2 | 8 | 2015-07-16
BC715C-2 | WJCMD WWTP | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 4035 | 4035 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-2 | WJCMD WWTP | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1368 | 1368 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-2 | WJCMD WWTP | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1271 | 1271 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-2 | WJCMD WWTP | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 90 | 90 |  | µg/L | 2 | 8 | 2015-07-16
BC715C-3 | KSWD WWTP | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 7220 | 7220 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-3 | KSWD WWTP | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5391 | 5391 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-3 | KSWD WWTP | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 299 | 299 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-3 | KSWD WWTP | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 297 | 297 |  | µg/L | 2 | 8 | 2015-07-16
BC715C-4 | GWSD WWTP | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 10556 | 10556 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-4 | GWSD WWTP | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9111 | 9111 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-4 | GWSD WWTP | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 57 | 57 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-4 | GWSD WWTP | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 72 | 72 |  | µg/L | 2 | 8 | 2015-07-16
BC715C-5 | Conifer Metro WWTP | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 6050 | 6050 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-5 | Conifer Metro WWTP | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4821 | 4821 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-5 | Conifer Metro WWTP | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 48 | 48 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-5 | Conifer Metro WWTP | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 58 | 58 |  | µg/L | 2 | 8 | 2015-07-16
BC715C-6 | Conifer High School | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 10654 | 10654 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-6 | Conifer High School | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7786 | 7786 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-6 | Conifer High School | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 993 | 993 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-6 | Conifer High School | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 169 | 169 |  | µg/L | 2 | 8 | 2015-07-16
BC715C-7 | Forest Hills WWTP | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 37700 | 37700 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-7 | Forest Hills WWTP | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 31216 | 31216 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-7 | Forest Hills WWTP | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 86 | 86 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-7 | Forest Hills WWTP | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 450 | 450 |  | µg/L | 2 | 8 | 2015-07-16
BC715C-8 | Morrison WWTP | 2015-07-09 | 2015-07-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 2287 | 2287 |  | µg/L | 6 | 42 | 2015-07-16
BC715C-8 | Morrison WWTP | 2015-07-09 | 2015-07-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 185 | 185 |  | µg/L | 2 | 8 | 2015-07-14
BC715C-8 | Morrison WWTP | 2015-07-09 | 2015-07-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 410 | 410 |  | µg/L | 5 | 35 | 2015-07-10
BC715C-8 | Morrison WWTP | 2015-07-09 | 2015-07-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 519 | 519 |  | µg/L | 2 | 8 | 2015-07-16
BC115B-1 | EMD WWTP | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 6806 | 6806 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-1 | EMD WWTP | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6089 | 6089 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-1 | EMD WWTP | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 121 | 121 |  | µg/L | 5 | 35 | 2015-09-11
BC115B-1 | EMD WWTP | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 79 | 79 |  | µg/L | 2 | 8 | 2015-09-25
BC115B-2 | WJCMD WWTP | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 7006 | 7006 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-2 | WJCMD WWTP | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1222 | 1222 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-2 | WJCMD WWTP | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4115 | 4115 |  | µg/L | 5 | 35 | 2015-09-11
BC115B-2 | WJCMD WWTP | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 1076 | 1076 |  | µg/L | 2 | 8 | 2015-09-25
BC115B-3 | KSWD WWTP | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 11071 | 11071 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-3 | KSWD WWTP | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7752 | 7752 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-3 | KSWD WWTP | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 441 | 441 |  | µg/L | 5 | 35 | 9/11/2015
BC115B-3 | KSWD WWTP | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 632 | 632 |  | µg/L | 2 | 8 | 2015-09-25
BC115B-4 | GWSD WWTP | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 10255 | 10255 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-4 | GWSD WWTP | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7676 | 7676 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-4 | GWSD WWTP | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 47 | 47 |  | µg/L | 5 | 35 | 2015-09-11
BC115B-4 | GWSD WWTP | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 214 | 214 |  | µg/L | 2 | 8 | 2015-09-25
BC115B-5 | Conifer Metro WWTP | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 8901 | 8901 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-5 | Conifer Metro WWTP | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 30 | 30 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-5 | Conifer Metro WWTP | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 8679 | 8679 |  | µg/L | 5 | 35 | 2015-09-11
BC115B-5 | Conifer Metro WWTP | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 93 | 93 |  | µg/L | 2 | 8 | 2015-09-25
BC115B-6 | Conifer High School | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 47756 | 47756 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-6 | Conifer High School | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 51972 | 51972 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-6 | Conifer High School | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 38 | 38 |  | µg/L | 5 | 35 | 2015-09-11
BC115B-6 | Conifer High School | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 562 | 562 |  | µg/L | 2 | 8 | 2015-09-25
BC115B-7 | Forest Hills WWTP | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 27421 | 27421 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-7 | Forest Hills WWTP | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 21698 | 21698 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-7 | Forest Hills WWTP | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 440 | 440 |  | µg/L | 5 | 35 | 2015-09-11
BC115B-7 | Forest Hills WWTP | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 531 | 531 |  | µg/L | 2 | 8 | 2015-09-25
BC115B-8 | Morrison WWTP | 2015-09-10 | 2015-09-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 2160 | 2160 |  | µg/L | 6 | 42 | 2015-10-08
BC115B-8 | Morrison WWTP | 2015-09-10 | 2015-09-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 670 | 670 |  | µg/L | 2 | 8 | 2015-09-15
BC115B-8 | Morrison WWTP | 2015-09-10 | 2015-09-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 305 | 305 |  | µg/L | 5 | 35 | 2015-09-11
BC115B-8 | Morrison WWTP | 2015-09-10 | 2015-09-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 1163 | 1163 |  | µg/L | 2 | 8 | 2015-09-25
BC1115-1 | EMD WWTP | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 8427 | 8427 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-1 | EMD WWTP | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7192 | 7192 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-1 | EMD WWTP | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 556 | 556 |  | µg/L | 5 | 35 | 2015-11-13
BC1115-1 | EMD WWTP | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 143 | 143 |  | µg/L | 2 | 8 | 2015-11-25
BC1115-2 | WJCMD WWTP | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 4206 | 4206 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-2 | WJCMD WWTP | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2282 | 2282 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-2 | WJCMD WWTP | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 508 | 508 |  | µg/L | 5 | 35 | 2015-11-13
BC1115-2 | WJCMD WWTP | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 121 | 121 |  | µg/L | 2 | 8 | 2015-11-25
BC1115-3 | KSWD WWTP | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 14434 | 14434 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-3 | KSWD WWTP | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 11188 | 11188 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-3 | KSWD WWTP | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 433 | 433 |  | µg/L | 5 | 35 | 2015-11-13
BC1115-3 | KSWD WWTP | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 343 | 343 |  | µg/L | 2 | 8 | 2015-11-25
BC1115-4 | GWSD WWTP | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 9315 | 9315 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-4 | GWSD WWTP | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7792 | 7792 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-4 | GWSD WWTP | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 55 | 55 |  | µg/L | 5 | 35 | 2015-11-13
BC1115-4 | GWSD WWTP | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 182 | 182 |  | µg/L | 2 | 8 | 2015-11-25
BC1115-5 | Conifer Metro WWTP | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 4239 | 4239 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-5 | Conifer Metro WWTP | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2768 | 2768 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-5 | Conifer Metro WWTP | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 51 | 51 |  | µg/L | 5 | 35 | 2015-11-13
BC1115-5 | Conifer Metro WWTP | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 219 | 219 |  | µg/L | 2 | 8 | 2015-11-25
BC1115-6 | Jeffco Public Schools | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 58772 | 58772 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-6 | Jeffco Public Schools | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 57697 | 57697 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-6 | Jeffco Public Schools | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 22 | 22 | J | µg/L | 5 | 35 | 2015-11-13
BC1115-6 | Jeffco Public Schools | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 276 | 276 |  | µg/L | 2 | 8 | 2015-11-25
BC1115-7 | Forest Hills WWTP | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 35599 | 35599 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-7 | Forest Hills WWTP | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 19875 | 19875 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-7 | Forest Hills WWTP | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 250 | 250 |  | µg/L | 5 | 35 | 2015-11-13
BC1115-7 | Forest Hills WWTP | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 961 | 961 |  | µg/L | 2 | 8 | 2015-11-25
BC1115-8 | Morrison WWTP | 2015-11-12 | 2015-11-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 1474 | 1474 |  | µg/L | 6 | 42 | 2015-11-25
BC1115-8 | Morrison WWTP | 2015-11-12 | 2015-11-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 52 | 52 |  | µg/L | 2 | 8 | 2015-11-13
BC1115-8 | Morrison WWTP | 2015-11-12 | 2015-11-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 145 | 145 |  | µg/L | 5 | 35 | 2015-11-13
BC1115-8 | Morrison WWTP | 2015-11-12 | 2015-11-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 221 | 221 |  | µg/L | 2 | 8 | 2015-11-25

## Regulation 85 2016
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE | [19 empty] | J |  | u |  |  |  |  | 2016
BC116-1 | EMD WWTP | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 14980 | 14980 |  | µg/L | 6 | 42 | 2016-01-21 | WWTF | Parameter | Method | MDL | PQL | unit | 2016-01-14 | 2016-03-10 | 2016-05-12 | 2016-07-14 | 2016-09-08 | 2016-11-10 | WWTF | Parameter | Method | MDL | PQL | unit | 2016-01-14 | 2016-03-10 | 2016-05-12 | 2016-07-14 | 2016-09-08 | 2016-11-10 |  |  | 2016-01-14 | 2016-03-10 | 2016-05-12 | 2016-07-14 | 2016-09-08 | 2016-11-10
BC116-1 | EMD WWTP | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 11995 | 11995 |  | µg/L | 2 | 8 | 2016-01-15 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 14980 | 12130 | 9169 | 7166 | 7735 | 9796 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 14.98 | 12.13 | 9.169 | 7.166 | 7.735 | 9.796 | Evergreen Metro District | CO-0031429 | 0.44 | 0.46 | 0.66 | 0.47 | 0.42 | 0.4
BC116-1 | EMD WWTP | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 670 | 670 |  | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 11995 | 9634 | 7727 | 6260 | 1865 | 5374 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.54 | 0.134 | 0.116 | 0.181 | 0.338 | 0.074 | West Jefferson County Metro District | CO-0020915 | 0.5 | 0.46 | 0.62 | 0.48 | 0.44 | 0.42
BC116-1 | EMD WWTP | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 540 | 540 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 670 | 2442 | 348 | 59 | 4695 | 4123 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 11.995 | 9.634 | 7.727 | 6.26 | 1.865 | 5.374 | Kittredge Water and Sanitation District | CO-0023841 | 0.07 | 0.07 | 0.11 | 0.45 | 0.51 | 0.2
BC116-2 | WJCMD WWTP | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 10607 | 10607 |  | µg/L | 6 | 42 | 2016-01-21 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 540 | 134 | 116 | 181 | 338 | 74 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.67 | 2.442 | 0.348 | 0.059 | 4.695 | 4.123 | Genesee Water and Sanitation District | CO-0022951 | 0.22 | 0.24 | 0.37 | 0.22 | 0.22 | 0.24
BC116-2 | WJCMD WWTP | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2441 | 2441 |  | µg/L | 2 | 8 | 2016-01-15 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 10607 | 4816 | 9119 | 2473 | 1634 | 3284 |  | TIN Calculated |  |  |  |  | 12.665 | 12.076 | 8.075 | 6.319 | 6.56 | 9.497 | Forest Hills Metro District | CO-0037044 | 0.018 | 0.02 | 0.019 | 0.017 | 0.018 | 0.018
BC116-2 | WJCMD WWTP | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 7172 | 7172 |  | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 2441 | 1546 | 649 | 931 | 333 | 1882 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 10.607 | 4.816 | 9.119 | 2.473 | 1.634 | 3.284 | Conifer Metro District | CO-0047295
BC116-2 | WJCMD WWTP | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 145 | 145 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 7172 | 1951 | 7295 | 507 | 154 | 125 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.145 | 0.197 | 0.488 | 0.132 | 0.145 | 0.173 | Conifer Sanitation Association | COX-047392 | 0.011 | 0.022 | 0.029 | 0.01 | 0.003 | 0.006
BC116-3 | KSWD WWTP | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 8449 | 8449 |  | µg/L | 6 | 42 | 2016-01-21 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 145 | 197 | 488 | 132 | 145 | 173 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 2.441 | 1.546 | 0.649 | 0.931 | 0.333 | 1.882 | JCS Conifer High School | CO-0047988
BC116-3 | KSWD WWTP | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5467 | 5467 |  | µg/L | 2 | 8 | 2016-01-15 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 8449 | 18675 | 9229 | 6328 | 5127 | 3932 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 7.172 | 1.951 | 7.295 | 0.507 | 0.154 | 0.125 | Morrison | CO-0041432 | 0.211 | 0.217 | 0.321 | 0.31 | 0.255 | 0.18
BC116-3 | KSWD WWTP | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 948 | 948 |  | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 5467 | 12916 | 7141 | 4222 | 2906 | 2612 |  | TIN Calculated |  |  |  |  | 9.613 | 3.497 | 7.944 | 1.438 | 0.487 | 2.007 | Mt. Evans Lab Jeffco Schools | COG589138
BC116-3 | KSWD WWTP | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 369 | 369 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 948 | 104 | 104 | 565 | 570 | 454 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 8.449 | 18.675 | 9.229 | 6.328 | 5.127 | 3.932
BC116-4 | GWSD WWTP | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 8356 | 8356 |  | µg/L | 6 | 42 | 2016-01-21 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 369 | 543 | 147 | 497 | 615 | 211 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.369 | 0.543 | 0.147 | 0.497 | 0.615 | 0.211 |  |  | Time | Sample type
BC116-4 | GWSD WWTP | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7063 | 7063 |  | µg/L | 2 | 8 | 2016-01-15 | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 8356 | 8822 | 7542 | 10987 | 10936 | 8465 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 5.467 | 12.916 | 7.141 | 4.222 | 2.906 | 2.612 | Evergreen Metro District | CO-0031429 | 9:00 | 12-hr
BC116-4 | GWSD WWTP | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 53 | 53 |  | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 7063 | 6524 | 6171 | 5625 | 8272 | 8149 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.948 | 0.104 | 0.104 | 0.565 | 0.57 | 0.454 | West Jefferson County Metro District | CO-0020915 | 9:00 | 12-hr
BC116-4 | GWSD WWTP | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 143 | 143 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 53 | 63 | 61 | 4475 | 110 | 75 |  | TIN Calculated |  |  |  |  | 6.415 | 13.02 | 7.245 | 4.787 | 3.476 | 3.066 | Kittredge Water and Sanitation District | CO-0023841 | 9:00 | 12-hr
BC116-5 | Conifer Metro WWTP | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 7631 | 7631 |  | µg/L | 6 | 42 | 2016-01-21 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 143 | 288 | 262 | 198 | 535 | 186 | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 8.356 | 8.822 | 7.542 | 10.987 | 10.936 | 8.465 | Genesee Water and Sanitation District | CO-0022951 | 8:00 | 24-hr
BC116-5 | Conifer Metro WWTP | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5555 | 5555 |  | µg/L | 2 | 8 | 2016-01-15 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 7631 | 7034 | 2014 | 25998 | 4979 | 3373 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.143 | 0.288 | 0.262 | 0.198 | 0.535 | 0.186 | Forest Hills Metro District | CO-0037044 | 10:00 | 12-hr
BC116-5 | Conifer Metro WWTP | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 80 | 80 |  | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 5555 | 5495 | 1445 | 23546 | 4416 | 3150 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 7.063 | 6.524 | 6.171 | 5.625 | 8.272 | 8.149 | Conifer Metro District | CO-047295
BC116-5 | Conifer Metro WWTP | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 252 | 252 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 80 | 68 | 23 | 47 | 63 |  |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.053 | 0.063 | 0.061 | 4.475 | 0.11 | 0.075 | Conifer Sanitation Association | COX-0047392 | 9:00 | grab
BC116-6 | Jeffco Public Schools | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 72157 | 72157 |  | µg/L | 6 | 42 | 2016-01-21 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 252 | 46 | 75 | 527 | 46 | 23 |  | TIN Calculated |  |  |  |  | 7.116 | 6.587 | 6.232 | 10.1 | 8.382 | 8.224 | JCS Conifer High School | CO-047988 | 9:00 | 12-hr
BC116-6 | Jeffco Public Schools | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 67050 | 67050 |  | µg/L | 2 | 8 | 2016-01-15 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 72157 | 87646 | 99363 |  | 96455 | 69942 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 7.631 | 7.034 | 2.014 | 25.998 | 4.979 | 3.373 | Morrison | CO-0041432 | 9:00 | 12-hr
BC116-6 | Jeffco Public Schools | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 21 | 21 | J | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 67050 | 80252 | 74861 |  | 53184 | 68644 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.252 | 0.046 | 0.075 | 0.527 | 0.046 | 0.023 | Mt. Evans Lab Jeffco Schools | COG589138 | 9:00 | grab
BC116-6 | Jeffco Public Schools | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 34 | 34 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 21 | 39 | 38 |  | 75 | 38 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 5.555 | 5.495 | 1.445 | 23.546 | 4.416 | 3.15
BC116-7 | Forest Hills WWTP | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 23701 | 23701 |  | µg/L | 6 | 42 | 2016-01-21 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 34 | 247 | 57 |  | 38 | 38 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.08 | 0.068 | 0.023 | 0.047 | 0.063 | 0 | Date Analyzed | TN | NO5 | NH3 | TP
BC116-7 | Forest Hills WWTP | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 20009 | 20009 |  | µg/L | 2 | 8 | 2016-01-15 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 23701 | 15206 | 22879 | 8884 | 38682 | 11943 |  | TIN Calculated |  |  |  |  | 5.635 | 5.563 | 1.468 | 23.593 | 4.479 | 3.15 |  | 2016-01-21 | 2016-01-15 | 2016-01-22 | 2016-01-21
BC116-7 | Forest Hills WWTP | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 90 | 90 |  | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 20009 | 10921 | 18626 | 7223 | 22974 | 11398 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 72.157 | 87.646 | 99.363 |  | 96.455 | 69.942 |  | 2016-03-16 | 2016-03-11 | 2016-03-17 | 2016-03-16
BC116-7 | Forest Hills WWTP | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 107 | 107 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 90 | 204 | 73 | 178 | 54 | 29 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.034 | 0.247 | 0.057 |  | 0.038 | 0.038 |  | 2016-05-18 | 2016-05-13 | 2016-05-20 | 2016-05-18
BC116-8 | Morrison WWTP | 2016-01-14 | 2016-01-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 3768 | 3768 |  | µg/L | 6 | 42 | 2016-01-21 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 107 | 423 | 605 | 163 | 724 | 543 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 67.05 | 80.252 | 74.861 |  | 53.184 | 68.644 |  | 2016-07-20 | 2016-07-15 | 2016-07-19 | 2016-07-20
BC116-8 | Morrison WWTP | 2016-01-14 | 2016-01-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 165 | 165 |  | µg/L | 2 | 8 | 2016-01-15 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 3768 | 2220 | 3364 | 4259 | 1074 | 4197 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.021 | 0.039 | 0.038 |  | 0.075 | 0.038 |  | 2016-09-21 | 2016-09-09 | 2016-09-20 | 2016-09-21
BC116-8 | Morrison WWTP | 2016-01-14 | 2016-01-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2479 | 2479 |  | µg/L | 5 | 35 | 2016-01-22 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 165 | 94 | 1648 | 2398 | 181 | 3402 |  | TIN Calculated |  |  |  |  | 67.071 | 80.291 | 74.899 |  | 53.259 | 68.682 |  | 2016-11-16 | 2016-11-11 | 2016-11-17 | 2016-11-16
BC116-8 | Morrison WWTP | 2016-01-14 | 2016-01-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 198 | 198 |  | µg/L | 2 | 8 | 2016-01-21 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 2479 | 513 | 105 | 226 | 140 | 104 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 23.701 | 15.206 | 22.879 | 8.884 | 38.682 | 11.943
[15 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 198 | 241 | 217 | 401 | 332 | 535 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.107 | 0.423 | 0.605 | 0.163 | 0.724 | 0.543 | Ammonia | Lachat 10-107-06-2-A
BC316B-1 | EMD WWTP | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 12130 | 12130 |  | µg/L | 6 | 42 | 2016-03-16 | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L |  | 39202 |  | 31415 | 39827 | 28834 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 20.009 | 10.921 | 18.626 | 7.223 | 22.974 | 11.398
BC316B-1 | EMD WWTP | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9634 | 9634 |  | µg/L | 2 | 8 | 2016-03-11 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L |  | 19 |  | 12559 | 22127 | 28289 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.09 | 0.204 | 0.073 | 0.178 | 0.054 | 0.029
BC316B-1 | EMD WWTP | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2442 | 2442 |  | µg/L | 5 | 35 | 2016-03-17 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L |  | 48993 |  | 54 | 51 | 38 |  | TIN Calculated |  |  |  |  | 20.099 | 11.125 | 18.699 | 7.401 | 23.028 | 11.427
BC316B-1 | EMD WWTP | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 134 | 134 |  | µg/L | 2 | 8 | 2016-03-16 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L |  | 406 |  | 353 | 1586 | 5824 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 3.768 | 2.22 | 3.364 | 4.259 | 1.074 | 4.197
BC316B-2 | WJCMD WWTP | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 4816 | 4816 |  | µg/L | 6 | 42 | 2016-03-16 | [13 empty] | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.198 | 0.241 | 0.217 | 0.401 | 0.332 | 0.535
BC316B-2 | WJCMD WWTP | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1546 | 1546 |  | µg/L | 2 | 8 | 2016-03-11 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 0.165 | 0.094 | 1.648 | 2.398 | 0.181 | 3.402
BC316B-2 | WJCMD WWTP | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1951 | 1951 |  | µg/L | 5 | 35 | 2016-03-17 | [13 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 2.479 | 0.513 | 0.105 | 0.226 | 0.14 | 0.104
BC316B-2 | WJCMD WWTP | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 197 | 197 |  | µg/L | 2 | 8 | 2016-03-16 | [13 empty] | TIN Calculated |  |  |  |  | 2.644 | 0.607 | 1.753 | 2.624 | 0.321 | 3.506
BC316B-3 | KSWD WWTP | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 18675 | 18675 |  | µg/L | 6 | 42 | 2016-03-16 | [12 empty] | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 0.002 | 0.008 | mg/l |  | 39.202 |  | 31.415 | 39.827 | 28.834
BC316B-3 | KSWD WWTP | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 12916 | 12916 |  | µg/L | 2 | 8 | 2016-03-11 | [13 empty] | Phosphorus, total | QC 10-115-01-4-B | 0 | 0 | mg/l |  | 0.406 |  | 0.353 | 1.586 | 5.824
BC316B-3 | KSWD WWTP | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 104 | 104 |  | µg/L | 5 | 35 | 2016-03-17 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.005 | 0.035 | mg/l |  | 0.019 |  | 12.559 | 22.127 | 28.289
BC316B-3 | KSWD WWTP | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 543 | 543 |  | µg/L | 2 | 8 | 2016-03-16 | [13 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.002 | 0.008 | mg/l |  | 48.993 |  | 0.054 | 0.051 | 0.038
BC316B-4 | GWSD WWTP | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 8822 | 8822 |  | µg/L | 6 | 42 | 2016-03-16 | [13 empty] | TIN Calculated | [5 empty] | 49.012 |  | 12.613 | 22.178 | 28.327
BC316B-4 | GWSD WWTP | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6524 | 6524 |  | µg/L | 2 | 8 | 2016-03-11
BC316B-4 | GWSD WWTP | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 63 | 63 |  | µg/L | 5 | 35 | 2016-03-17
BC316B-4 | GWSD WWTP | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 288 | 288 |  | µg/L | 2 | 8 | 2016-03-16
BC316B-5 | Conifer Metro WWTP | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 7034 | 7034 |  | µg/L | 6 | 42 | 2016-03-16
BC316B-5 | Conifer Metro WWTP | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5495 | 5495 |  | µg/L | 2 | 8 | 2016-03-11
BC316B-5 | Conifer Metro WWTP | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 68 | 68 |  | µg/L | 5 | 35 | 2016-03-17
BC316B-5 | Conifer Metro WWTP | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 46 | 46 |  | µg/L | 2 | 8 | 2016-03-16
BC316B-6 | Jeffco Public Schools | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 87646 | 87646 |  | µg/L | 6 | 42 | 2016-03-16
BC316B-6 | Jeffco Public Schools | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 80252 | 80252 |  | µg/L | 2 | 8 | 2016-03-11
BC316B-6 | Jeffco Public Schools | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 39 | 39 |  | µg/L | 5 | 35 | 2016-03-17
BC316B-6 | Jeffco Public Schools | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 247 | 247 |  | µg/L | 2 | 8 | 2016-03-16
BC316B-7 | Forest Hills WWTP | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 15206 | 15206 |  | µg/L | 6 | 42 | 2016-03-16
BC316B-7 | Forest Hills WWTP | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 10921 | 10921 |  | µg/L | 2 | 8 | 2016-03-11
BC316B-7 | Forest Hills WWTP | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 204 | 204 |  | µg/L | 5 | 35 | 2016-03-17
BC316B-7 | Forest Hills WWTP | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 423 | 423 |  | µg/L | 2 | 8 | 2016-03-16
BC316B-8 | Morrison WWTP | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 2220 | 2220 |  | µg/L | 6 | 42 | 2016-03-16
BC316B-8 | Morrison WWTP | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 94 | 94 |  | µg/L | 2 | 8 | 2016-03-11
BC316B-8 | Morrison WWTP | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 513 | 513 |  | µg/L | 5 | 35 | 2016-03-17
BC316B-8 | Morrison WWTP | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 241 | 241 |  | µg/L | 2 | 8 | 2016-03-16
BC316B-9 | Mt. Evans Lab Jeffco Schools | 2016-03-10 | 2016-03-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 39202 | 39202 |  | µg/L | 6 | 42 | 2016-03-16
BC316B-9 | Mt. Evans Lab Jeffco Schools | 2016-03-10 | 2016-03-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 19 | 19 |  | µg/L | 2 | 8 | 2016-03-11
BC316B-9 | Mt. Evans Lab Jeffco Schools | 2016-03-10 | 2016-03-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 48993 | 48993 |  | µg/L | 5 | 35 | 2016-03-17
BC316B-9 | Mt. Evans Lab Jeffco Schools | 2016-03-10 | 2016-03-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 406 | 406 |  | µg/L | 2 | 8 | 2016-03-16
BC516B-1 | EMD WWTP | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 9169 | 9169 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-1 | EMD WWTP | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7727 | 7727 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-1 | EMD WWTP | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 348 | 348 |  | µg/L | 5 | 35 | 2016-05-20
BC516B-1 | EMD WWTP | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 116 | 116 |  | µg/L | 2 | 8 | 2016-05-18
BC516B-2 | WJCMD WWTP | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 9119 | 9119 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-2 | WJCMD WWTP | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 649 | 649 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-2 | WJCMD WWTP | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 7295 | 7295 |  | µg/L | 5 | 35 | 2016-05-20
BC516B-2 | WJCMD WWTP | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 488 | 488 |  | µg/L | 2 | 8 | 2016-05-18
BC516B-3 | KSWD WWTP | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 9229 | 9229 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-3 | KSWD WWTP | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7141 | 7141 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-3 | KSWD WWTP | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 104 | 104 |  | µg/L | 5 | 35 | 2016-05-20
BC516B-3 | KSWD WWTP | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 147 | 147 |  | µg/L | 2 | 8 | 2016-05-18
BC516B-4 | GWSD WWTP | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 7542 | 7542 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-4 | GWSD WWTP | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6171 | 6171 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-4 | GWSD WWTP | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 61 | 61 |  | µg/L | 5 | 35 | 2016-05-20
BC516B-4 | GWSD WWTP | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 262 | 262 |  | µg/L | 2 | 8 | 2016-05-18
BC516B-5 | Conifer Metro WWTP | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 2014 | 2014 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-5 | Conifer Metro WWTP | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1445 | 1445 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-5 | Conifer Metro WWTP | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 23 | 23 | J | µg/L | 5 | 35 | 2016-05-20
BC516B-5 | Conifer Metro WWTP | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 75 | 75 |  | µg/L | 2 | 8 | 2016-05-18
BC516B-6 | Jeffco Public Schools | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 99363 | 99363 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-6 | Jeffco Public Schools | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 74861 | 74861 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-6 | Jeffco Public Schools | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 38 | 38 |  | µg/L | 5 | 35 | 2016-05-20
BC516B-6 | Jeffco Public Schools | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 57 | 57 |  | µg/L | 2 | 8 | 2016-05-18
BC516B-7 | Forest Hills WWTP | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 22879 | 22879 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-7 | Forest Hills WWTP | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 18626 | 18626 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-7 | Forest Hills WWTP | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 73 | 73 |  | µg/L | 5 | 35 | 2016-05-20
BC516B-7 | Forest Hills WWTP | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 605 | 605 |  | µg/L | 2 | 8 | 2016-05-18
BC516B-8 | Morrison WWTP | 2016-05-12 | 2016-05-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 3364 | 3364 |  | µg/L | 6 | 42 | 2016-05-18
BC516B-8 | Morrison WWTP | 2016-05-12 | 2016-05-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1648 | 1648 |  | µg/L | 2 | 8 | 2016-05-13
BC516B-8 | Morrison WWTP | 2016-05-12 | 2016-05-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 105 | 105 |  | µg/L | 5 | 35 | 2016-05-20
BC516B-8 | Morrison WWTP | 2016-05-12 | 2016-05-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 217 | 217 |  | µg/L | 2 | 8 | 2016-05-18
BC716D-1 | EMD WWTP | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 7166 | 7166 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-1 | EMD WWTP | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6260 | 6260 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-1 | EMD WWTP | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 59 | 59 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-1 | EMD WWTP | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 181 | 181 |  | µg/L | 2 | 8 | 2016-07-20
BC716D-2 | WJCMD WWTP | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 2473 | 2473 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-2 | WJCMD WWTP | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 931 | 931 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-2 | WJCMD WWTP | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 507 | 507 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-2 | WJCMD WWTP | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 132 | 132 |  | µg/L | 2 | 8 | 2016-07-20
BC716D-3 | KSWD WWTP | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 6328 | 6328 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-3 | KSWD WWTP | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4222 | 4222 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-3 | KSWD WWTP | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 565 | 565 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-3 | KSWD WWTP | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 497 | 497 |  | µg/L | 2 | 8 | 2016-07-20
BC716D-4 | GWSD WWTP | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 10987 | 10987 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-4 | GWSD WWTP | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5625 | 5625 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-4 | GWSD WWTP | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4475 | 4475 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-4 | GWSD WWTP | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 198 | 198 |  | µg/L | 2 | 8 | 2016-07-20
BC716D-5 | Forest Hills WWTP | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 25998 | 25998 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-5 | Forest Hills WWTP | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 23546 | 23546 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-5 | Forest Hills WWTP | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 47 | 47 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-5 | Forest Hills WWTP | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 527 | 527 |  | µg/L | 2 | 8 | 2016-07-20
BC716D-6 | Conifer Metro WWTP | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 8884 | 8884 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-6 | Conifer Metro WWTP | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7223 | 7223 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-6 | Conifer Metro WWTP | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 178 | 178 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-6 | Conifer Metro WWTP | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 163 | 163 |  | µg/L | 2 | 8 | 2016-07-20
BC716D-7 | JCS Outdoor Lab | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 31415 | 31415 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-7 | JCS Outdoor Lab | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 12559 | 12559 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-7 | JCS Outdoor Lab | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 54 | 54 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-7 | JCS Outdoor Lab | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 353 | 353 |  | µg/L | 2 | 8 | 2016-07-20
BC716D-8 | Morrison WWTP | 2016-07-14 | 2016-07-14 | Total Nitrogen | SW | QC 10-107-04-4-B | 4259 | 4259 |  | µg/L | 6 | 42 | 2016-07-20
BC716D-8 | Morrison WWTP | 2016-07-14 | 2016-07-14 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2398 | 2398 |  | µg/L | 2 | 8 | 2016-07-15
BC716D-8 | Morrison WWTP | 2016-07-14 | 2016-07-14 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 226 | 226 |  | µg/L | 5 | 35 | 2016-07-19
BC716D-8 | Morrison WWTP | 2016-07-14 | 2016-07-14 | Phosphorus, total | SW | QC 10-115-01-4-B | 401 | 401 |  | µg/L | 2 | 8 | 2016-07-20
BC916-1 | EMD WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 7735 | 7735 |  | µg/L | 6 | 42 | 2016-09-21
BC916-1 | EMD WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1865 | 1865 |  | µg/L | 2 | 8 | 2016-09-09
BC916-1 | EMD WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4695 | 4695 |  | µg/L | 5 | 35 | 2016-09-20
BC916-1 | EMD WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 338 | 338 |  | µg/L | 2 | 8 | 2016-09-21
BC916-2 | WJCMD WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1634 | 1634 |  | µg/L | 6 | 42 | 2016-09-21
BC916-2 | WJCMD WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 333 | 333 |  | µg/L | 2 | 8 | 2016-09-09
BC916-2 | WJCMD WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 154 | 154 |  | µg/L | 5 | 35 | 2016-09-20
BC916-2 | WJCMD WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 145 | 145 |  | µg/L | 2 | 8 | 2016-09-21
BC916-3 | KSWD WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 5127 | 5127 |  | µg/L | 6 | 42 | 2016-09-21
BC916-3 | KSWD WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2906 | 2906 |  | µg/L | 2 | 8 | 2016-09-09
BC916-3 | KSWD WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 570 | 570 |  | µg/L | 5 | 35 | 2016-09-20
BC916-3 | KSWD WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 615 | 615 |  | µg/L | 2 | 8 | 2016-09-21
BC916-4 | GWSD WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 10936 | 10936 |  | µg/L | 6 | 42 | 2016-09-21
BC916-4 | GWSD WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 8272 | 8272 |  | µg/L | 2 | 8 | 2016-09-09
BC916-4 | GWSD WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 110 | 110 |  | µg/L | 5 | 35 | 2016-09-20
BC916-4 | GWSD WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 535 | 535 |  | µg/L | 2 | 8 | 2016-09-21
BC916-6 | Conifer Metro WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 4979 | 4979 |  | µg/L | 6 | 42 | 2016-09-29
BC916-6 | Conifer Metro WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4416 | 4416 |  | µg/L | 2 | 8 | 2016-09-09
BC916-6 | Conifer Metro WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 63 | 63 |  | µg/L | 5 | 35 | 2016-09-20
BC916-6 | Conifer Metro WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 46 | 46 |  | µg/L | 2 | 8 | 2016-09-21
BC916-9 | Conifer H.S. WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 96455 | 96455 |  | µg/L | 6 | 42 | 2016-09-21
BC916-9 | Conifer H.S. WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 53184 | 53184 |  | µg/L | 2 | 8 | 2016-09-09
BC916-9 | Conifer H.S. WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 75 | 75 |  | µg/L | 5 | 35 | 2016-09-20
BC916-9 | Conifer H.S. WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 38 | 38 |  | µg/L | 2 | 8 | 2016-09-21
BC916-8 | Forest Hills WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 38682 | 38682 |  | µg/L | 6 | 42 | 2016-09-21
BC916-8 | Forest Hills WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 22974 | 22974 |  | µg/L | 2 | 8 | 2016-09-09
BC916-8 | Forest Hills WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 54 | 54 |  | µg/L | 5 | 35 | 2016-09-20
BC916-8 | Forest Hills WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 724 | 724 |  | µg/L | 2 | 8 | 2016-09-21
BC916-5 | Morrison WWTP | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1074 | 1074 |  | µg/L | 6 | 42 | 2016-09-21
BC916-5 | Morrison WWTP | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 181 | 181 |  | µg/L | 2 | 8 | 2016-09-09
BC916-5 | Morrison WWTP | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 140 | 140 |  | µg/L | 5 | 35 | 2016-09-20
BC916-5 | Morrison WWTP | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 332 | 332 |  | µg/L | 2 | 8 | 2016-09-21
BC916-7 | Mt. Evans Lab Jeffco | 2016-09-08 | 2016-09-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 39827 | 39827 |  | µg/L | 6 | 42 | 2016-09-21
BC916-7 | Mt. Evans Lab Jeffco | 2016-09-08 | 2016-09-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 22127 | 22127 |  | µg/L | 2 | 8 | 2016-09-09
BC916-7 | Mt. Evans Lab Jeffco | 2016-09-08 | 2016-09-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 51 | 51 |  | µg/L | 5 | 35 | 2016-09-20
BC916-7 | Mt. Evans Lab Jeffco | 2016-09-08 | 2016-09-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 1586 | 1586 |  | µg/L | 2 | 8 | 2016-09-21
BC1116-1 | EMD WWTP | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 9796 | 9796 |  | µg/L | 6 | 42 | 2016-11-16
BC1116-1 | EMD WWTP | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5374 | 5374 |  | µg/L | 2 | 8 | 2016-11-11
BC1116-1 | EMD WWTP | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4123 | 4123 |  | µg/L | 5 | 35 | 2016-11-17
BC1116-1 | EMD WWTP | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 74 | 74 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-2 | WJCMD WWTP | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 3284 | 3284 |  | µg/L | 6 | 42 | 2016-11-16
BC1116-2 | WJCMD WWTP | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1882 | 1882 |  | µg/L | 2 | 8 | 2016-11-11
BC1116-2 | WJCMD WWTP | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 125 | 125 |  | µg/L | 5 | 35 | 2016-11-17
BC1116-2 | WJCMD WWTP | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 173 | 173 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-3 | KSWD WWTP | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 3932 | 3932 |  | µg/L | 6 | 42 | 2016-11-16
BC1116-3 | KSWD WWTP | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2612 | 2612 |  | µg/L | 2 | 8 | 2016-11-11
BC1116-3 | KSWD WWTP | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 454 | 454 |  | µg/L | 5 | 35 | 2016-11-17
BC1116-3 | KSWD WWTP | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 211 | 211 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-4 | GWSD WWTP | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 8465 | 8465 |  | µg/L | 6 | 42 | 2016-11-16
BC1116-4 | GWSD WWTP | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 8149 | 8149 |  | µg/L | 2 | 8 | 2016-11-11
BC1116-4 | GWSD WWTP | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 75 | 75 |  | µg/L | 5 | 35 | 2016-11-17
BC1116-4 | GWSD WWTP | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 186 | 186 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-6 | Conifer Metro WWTP | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 3373 | 3373 |  | µg/L | 6 | 42 | 2016-11-16
BC1116-6 | Conifer Metro WWTP | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3150 | 3150 |  | µg/L | 2 | 8 | 2016-11-11
BC1116-6 | Conifer Metro WWTP | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A |  |  | U | µg/L | 5 | 35 | 2016-11-17
BC1116-6 | Conifer Metro WWTP | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 23 | 23 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-7 | Conifer H.S. WWTP | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 69942 | 69942 |  | µg/L | 6 | 42 | 2016-11-23
BC1116-7 | Conifer H.S. WWTP | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 68644 | 68644 |  | µg/L | 2 | 8 | 2016-11-18
BC1116-7 | Conifer H.S. WWTP | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 38 | 38 |  | µg/L | 5 | 35 | 2016-11-17
BC1116-7 | Conifer H.S. WWTP | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 38 | 38 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-9 | Forest Hills WWTP | 2016-11-09 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 11943 | 11943 |  | µg/L | 6 | 42 | 2016-11-23
BC1116-9 | Forest Hills WWTP | 2016-11-09 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 11398 | 11398 |  | µg/L | 2 | 8 | 2016-11-18
BC1116-9 | Forest Hills WWTP | 2016-11-09 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 29 | 29 | J | µg/L | 5 | 35 | 2016-11-17
BC1116-9 | Forest Hills WWTP | 2016-11-09 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 543 | 543 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-5 | Morrison WWTP | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 4197 | 4197 |  | µg/L | 6 | 42 | 2016-11-16
BC1116-5 | Morrison WWTP | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3402 | 3402 |  | µg/L | 2 | 8 | 2016-11-11
BC1116-5 | Morrison WWTP | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 104 | 104 |  | µg/L | 5 | 35 | 2016-11-17
BC1116-5 | Morrison WWTP | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 535 | 535 |  | µg/L | 2 | 8 | 2016-11-16
BC1116-8 | Mt. Evans Lab Jeffco | 2016-11-10 | 2016-11-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 28834 | 28834 |  | µg/L | 6 | 42 | 2016-11-23
BC1116-8 | Mt. Evans Lab Jeffco | 2016-11-10 | 2016-11-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 28289 | 28289 |  | µg/L | 2 | 8 | 2016-11-18
BC1116-8 | Mt. Evans Lab Jeffco | 2016-11-10 | 2016-11-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 38 | 38 |  | µg/L | 5 | 35 | 2016-11-17
BC1116-8 | Mt. Evans Lab Jeffco | 2016-11-10 | 2016-11-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 5824 | 5824 |  | µg/L | 2 | 8 | 2016-11-16

## Rgulation 85 2017
|  | Time | Sample type | Notes |  |  | 0.0148 | [6 empty] | WWTF | Parameter | Method | MDL | PQL | unit | 2017-01-12 | 2017-03-09 | 2017-05-04 | 2017-07-06 | 2017-09-07 | 2017-11-09 | WWTF | Parameter | Method | MDL | PQL | unit | 2017-01-12 | 2017-03-09 | 2017-05-04 | 2017-07-06 | 2017-09-06 | 2017-11-09
Evergreen Metro District | CO-0031429 | 9:00 | 12-hr | [10 empty] | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 8098 | 10275 | 9911 | 7004 | 7582 | 8795 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 8.098 | 10.275 | 9.911 | 7.004 | 7.582 | 8.795
West Jefferson County Metro District | CO-0020915 | 9:00 | 12-hr | [11 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 6275 | 5562 | 9238 | 6411 | 6954 | 5513 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 6.275 | 5.562 | 9.238 | 6.411 | 6.954 | 5.513
Kittredge Water and Sanitation District | CO-0023841 | 9:00 | 12-hr | [11 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 46 | 2677 | 99 | 58 | 117 | 2189 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.046 | 2.677 | 0.099 | 0.058 | 0.117 | 2.189
Genesee Water and Sanitation District | CO-0022951 | 8:00 | 24-hr | [11 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 239 | 134 | 230 | 78 | 94 | 180 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.239 | 0.134 | 0.23 | 0.078 | 0.094 | 0.18
Forest Hills Metro District | CO-0037044 | 10:00 | 12-hr | [10 empty] | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 19262 | 7597 | 2395 | 2495 | 2986 | 4550 |  | TIN Calculated |  |  |  |  | 6.321 | 8.239 | 9.337 | 6.469 | 7.071 | 7.702
Conifer Metro District | CO-047295 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 493 | 3613 | 1084 | 600 | 1429 | 3505 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 19.262 | 7.597 | 2.395 | 2.495 | 2.986 | 4.55
Conifer Sanitation Association | COX-0047392 | 9:00 | grab | [11 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 18392 | 1995 | 210 | 579 | 546 | 70 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 0.493 | 3.613 | 1.084 | 0.6 | 1.429 | 3.505
JCS Conifer High School | CO-047988 | 9:00 | 12-hr | [11 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 247 | 145 | 99 | 197 | 196 | 137 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 18.392 | 1.995 | 0.21 | 0.579 | 0.546 | 0.07
Morrison | CO-0041432 | 9:00 | 12-hr | 5/4/2017 Grab 12:00 | [9 empty] | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 9643 | 10269 | 6953 | 3966 | 10930 | 5901 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.247 | 0.145 | 0.099 | 0.197 | 0.196 | 0.137
Mt. Evans Lab Jeffco Schools | COG589138 | 9:00 | grab | [11 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 5479 | 8087 | 4979 | 1965 | 9209 | 4541 |  | TIN Calculated |  |  |  |  | 18.885 | 5.608 | 1.294 | 1.179 | 1.975 | 3.575
[15 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 2668 | 113 | 485 | 1013 | 88 | 414 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 9.643 | 10.269 | 6.953 | 3.966 | 10.93 | 5.901
24-hr WW Flows MGD | Permit | 2017-01-12 | 2017-03-09 | 2017-05-04 | 2017-07-06 | 2017-09-07 | 2017-11-09 | [7 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 310 | 184 | 221 | 256 | 1258 | 186 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 5.479 | 8.087 | 4.979 | 1.965 | 9.209 | 4.541
Evergreen Metro District | CO-0031429 | 0.4032 | 0.4594 | 0.4387 | 0.47 | 0.4688 | 0.45 | [6 empty] | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 8667 | 9600 | 7424 | 8175 | 10930 | 8547 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 2.668 | 0.113 | 0.485 | 1.013 | 0.088 | 0.414
West Jefferson County Metro District | CO-0020915 | 0.5071 | 0.4683 | 0.4748 | 0.47 | 0.38 | 0.67 | [7 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 6868 | 4280 | 6702 | 7961 | 88 | 7912 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.31 | 0.184 | 0.221 | 0.256 | 1.258 | 0.186
Kittredge Water and Sanitation District | CO-0023841 | 0.05784 | 0.05083 | 0.03741 | 0.05 | 0.06 | 0.05 | [7 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 80 | 4275 | 116 | 91 | 9209 | 69 |  | TIN Calculated |  |  |  |  | 8.147 | 8.2 | 5.464 | 2.978 | 9.297 | 4.955
Genesee Water and Sanitation District | CO-0022951 | 0.24 | 0.23 | 0.24 | 0.28 | 0.32 | 0.28 | [7 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 498 | 186 | 200 | 358 | 1258 | 366 | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 8.667 | 9.6 | 7.424 | 8.175 | 10.93 | 8.547
Forest Hills Metro District | CO-0037044 | 0.017427 | 0.016255 | 0.017404 | 0.016992 | 0.019464 | 0.014466 | [6 empty] | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 5810 | 7008 | 8672 | 859 | 1799 | 1778 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 6.868 | 4.28 | 6.702 | 7.961 | 0.088 | 7.912
Conifer Metro District | COX-047392 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 4295 | 4400 | 5600 | 463 | 1011 | 1338 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.08 | 4.275 | 0.116 | 0.091 | 9.209 | 0.069
Conifer Sanitation Association | COG-589060 | 0.0072 | 0.0072 | 0.0045 | 0.019 | 0.0072 | 0.0072 | [7 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 38 | 51 | 31 | 244 | 46 | 5 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.498 | 0.186 | 0.2 | 0.358 | 1.258 | 0.366 |  |  |  | MDL | PQL
JCS Conifer High School | CO-0047988 | 0.0148 | 0.00317 | 0.00444 | 0.0041 | 0.00184 | 0.00356 | [7 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 245 | 343 | 771 | 21 | 63 | 28 |  | TIN Calculated |  |  |  |  | 6.948 | 8.555 | 6.818 | 8.052 | 9.297 | 7.981 | Total Nitrogen | QC 10-107-04-4-B | mg/l | 6 | 42
Morrison | CO-0041432 | 0.08 | 0.09 | 0.08 | 0.15 | 0.14 | 0.07 | [6 empty] | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 73149 | 91426 | 86825 | 10170 | 67528 | 83751 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 5.81 | 7.008 | 8.672 | 0.859 | 1.799 | 1.778 | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | mg/l | 2 | 8
Mt. Evans Lab Jeffco Schools | COG589138 | 0.0012 | 0.0036 | 0.0041 | 0.0036 | 0.0029 | 0.0015 | [7 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 65510 | 86674 | 83360 | 9054 | 63197 | 81539 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 4.295 | 4.4 | 5.6 | 0.463 | 1.011 | 1.338 | Nitrogen, ammonia | QC 10-107-06-2-A | mg/l | 5 | 35
[11 empty] | MDL | PGL |  |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 46 | 27 | 38 | 58 | 47 | 31 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.038 | 0.051 | 0.031 | 0.244 | 0.046 | 0.005 | Phosphorus, total | QC 10-115-01-4-B | mg/l | 2 | 8
BC117B-1 | EMD WWTP | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 8098 | 8098 |  | µg/L | 6 | 42 | 2017-01-18 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 28 | 31 | 71 | 434 | 93 | 48 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.245 | 0.343 | 0.771 | 0.021 | 0.063 | 0.028
BC117B-1 | EMD WWTP | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6275 | 6275 |  | µg/L | 2 | 8 | 2017-01-13 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 12846 | 21407 | 5647 | 4050 | 17855 | 16250 |  | TIN Calculated |  |  |  |  | 4.333 | 4.451 | 5.631 | 0.707 | 1.057 | 1.343
BC117B-1 | EMD WWTP | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 46 | 46 |  | µg/L | 5 | 35 | 2017-01-19 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 10908 | 16185 | 3662 | 1817 | 17796 | 15190 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 73.149 | 91.426 | 86.825 | 10.17 | 67.528 | 83.751
BC117B-1 | EMD WWTP | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 239 | 239 |  | µg/L | 2 | 8 | 2017-01-18 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 18 | 2401 | 306 | 369 | 99 | 270 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 65.51 | 86.674 | 83.36 | 9.054 | 63.197 | 81.539
BC117B-2 | WJCMD WWTP | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 19262 | 19262 |  | µg/L | 6 | 42 | 2017-01-18 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 423 | 460 | 610 | 309 | 790 | 880 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.046 | 0.027 | 0.038 | 0.058 | 0.047 | 0.031
BC117B-2 | WJCMD WWTP | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 493 | 493 |  | µg/L | 2 | 8 | 2017-01-13 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 1656 | 3461 | 7054 | 36273 | 2317 | 2454 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.028 | 0.031 | 0.071 | 0.434 | 0.093 | 0.048
BC117B-2 | WJCMD WWTP | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 18392 | 18392 |  | µg/L | 5 | 35 | 2017-01-19 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 147 | 151 | 697 | 33418 | 1474 | 852 | [6 empty] | 65.556 | 86.701 | 83.398 | 9.112 | 63.244 | 81.57
BC117B-2 | WJCMD WWTP | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 247 | 247 |  | µg/L | 2 | 8 | 2017-01-18 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 50 | 1124 | 4808 | 204 | 86 | 160 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 12.846 | 21.407 | 5.647 | 4.05 | 17.855 | 16.25
BC117B-3 | KSWD WWTP | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 9643 | 9643 |  | µg/L | 6 | 42 | 2017-01-18 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 306 | 305 | 1295 | 662 | 260 | 476 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 10.908 | 16.185 | 3.662 | 1.817 | 17.796 | 15.19
BC117B-3 | KSWD WWTP | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5479 | 5479 |  | µg/L | 2 | 8 | 2017-01-13 | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 43165 | 40847 | 30415 | 57949 | 57949 | 38717 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.018 | 2.401 | 0.306 | 0.369 | 0.099 | 0.27
BC117B-3 | KSWD WWTP | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2668 | 2668 |  | µg/L | 5 | 35 | 2017-01-19 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 38532 | 39069 | 28958 | 56016 | 56016 | 34284 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.423 | 0.46 | 0.61 | 0.309 | 0.79 | 0.88
BC117B-3 | KSWD WWTP | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 310 | 310 |  | µg/L | 2 | 8 | 2017-01-18 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 395 | 39 | 130 | 43 | 43 | 20 |  | TIN Calculated |  |  |  |  | 10.926 | 18.586 | 3.968 | 2.186 | 17.895 | 15.46
BC117B-4 | GWSD WWTP | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 8667 | 8667 |  | µg/L | 6 | 42 | 2017-01-18 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 105 | 723 | 224 | 175 | 175 | 165 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 1.656 | 3.461 | 7.054 | 36.273 | 2.317 | 2.454
BC117B-4 | GWSD WWTP | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6868 | 6868 |  | µg/L | 2 | 8 | 2017-01-13 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 0.147 | 0.151 | 0.697 | 33.418 | 1.474 | 0.852
BC117B-4 | GWSD WWTP | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 80 | 80 |  | µg/L | 5 | 35 | 2017-01-19 | [13 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.05 | 1.124 | 4.808 | 0.204 | 0.086 | 0.16
BC117B-4 | GWSD WWTP | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 498 | 498 |  | µg/L | 2 | 8 | 2017-01-18 | [13 empty] | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.306 | 0.305 | 1.295 | 0.662 | 0.26 | 0.476
BC117B-5 | CSA WWTP | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 5810 | 5810 |  | µg/L | 6 | 42 | 2017-01-18 | WWTF | Parameter | Method | MDL | PQL | unit | 2017-01-12 | 2017-03-09 | 2017-05-04 | 2017-07-06 | 2017-09-07 | 2017-11-09 |  | TIN Calculated |  |  |  |  | 0.197 | 1.275 | 5.505 | 33.622 | 1.56 | 1.012
BC117B-5 | CSA WWTP | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4295 | 4295 |  | µg/L | 2 | 8 | 2017-01-13 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 12.846 | 21.407 | 5.647 | 4.05 | 17.855 | 16.25 | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 43.165 | 40.847 | 30.415 | 57.949 | 57.949 | 38.717
BC117B-5 | CSA WWTP | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 38 | 38 |  | µg/L | 5 | 35 | 2017-01-19 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 10.908 | 16.185 | 3.662 | 1.817 | 17.796 | 15.19 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 38.532 | 39.069 | 28.958 | 56.016 | 56.016 | 34.284
BC117B-5 | CSA WWTP | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 245 | 245 |  | µg/L | 2 | 8 | 2017-01-18 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.018 | 2.401 | 0.306 | 0.369 | 0.099 | 0.27 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.395 | 0.039 | 0.13 | 0.043 | 0.043 | 0.02
BC117B-9 | Conifer H.S. | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 73149 | 73149 |  | µg/L | 6 | 42 | 2017-01-18 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.423 | 0.46 | 0.61 | 0.309 | 0.79 | 0.88 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.105 | 0.723 | 0.224 | 0.175 | 0.175 | 0.165
BC117B-9 | Conifer H.S. | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 65510 | 65510 |  | µg/L | 2 | 8 | 2017-01-13 |  | TIN Calculated |  |  |  |  | 10.926 | 18.586 | 3.968 | 2.186 | 17.895 | 15.46 |  | TIN Calculated |  |  |  |  | 38.927 | 39.108 | 29.088 | 56.059 | 56.059 | 34.304
BC117B-9 | Conifer H.S. | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 46 | 46 |  | µg/L | 5 | 35 | 2017-01-19 | [6 empty] | 2016-01-14 | 2016-03-10 | 2016-05-12 | 2016-07-14 | 2016-09-08 | 2016-11-10
BC117B-9 | Conifer H.S. | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 28 | 28 |  | µg/L | 2 | 8 | 2017-01-18 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 23.701 | 15.206 | 22.879 | 8.884 | 38.682 | 11.943
BC117B-7 | Forest Hills WWTP | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 12846 | 12846 |  | µg/L | 6 | 42 | 2017-01-18 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.107 | 0.423 | 0.605 | 0.163 | 0.724 | 0.543
BC117B-7 | Forest Hills WWTP | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 10908 | 10908 |  | µg/L | 2 | 8 | 2017-01-13 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 20.009 | 10.921 | 18.626 | 7.223 | 22.974 | 11.398
BC117B-7 | Forest Hills WWTP | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 18 | 18 | J | µg/L | 5 | 35 | 2017-01-19 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.09 | 0.204 | 0.073 | 0.178 | 0.054 | 0.029
BC117B-7 | Forest Hills WWTP | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 423 | 423 |  | µg/L | 2 | 8 | 2017-01-18 |  | TIN Calculated |  |  |  |  | 20.099 | 11.125 | 18.699 | 7.401 | 23.028 | 11.427
BC117B-8 | Morrison WWTP | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 1656 | 1656 |  | µg/L | 6 | 42 | 2017-01-18 | [6 empty] | 2015-01-08 | 2015-03-12 | 2015-05-14 | 2015-07-09 | 2015-09-10 | 2015-11-12
BC117B-8 | Morrison WWTP | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 147 | 147 |  | µg/L | 2 | 8 | 2017-01-13 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 28.43 | 20.995 | 16.413 | 37.7 | 27.421 | 35.599
BC117B-8 | Morrison WWTP | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 50 | 50 |  | µg/L | 5 | 35 | 2017-01-19 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.255 | 0.329 | 0.437 | 0.45 | 0.531 | 0.961
BC117B-8 | Morrison WWTP | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 306 | 306 |  | µg/L | 2 | 8 | 2017-01-18 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 24.294 | 18.316 | 12.75 | 31.216 | 21.698 | 19.875
BC117B-6 | Mt. Evans Lab | 2017-01-12 | 2017-01-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 43165 | 43165 |  | µg/L | 6 | 42 | 2017-01-18 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.147 | 1.489 | 0.947 | 0.086 | 0.44 | 0.25
BC117B-6 | Mt. Evans Lab | 2017-01-12 | 2017-01-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 38532 | 38532 |  | µg/L | 2 | 8 | 2017-01-13 |  | TIN Calculated |  |  |  |  | 24.441 | 19.805 | 13.697 | 31.302 | 22.138 | 20.125
BC117B-6 | Mt. Evans Lab | 2017-01-12 | 2017-01-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 395 | 395 |  | µg/L | 5 | 35 | 2017-01-19 | [6 empty] | 2014-01-09 | 2014-03-13 | 2014-05-08 | 2014-07-10 | 2014-09-11 | 2014-11-13
BC117B-6 | Mt. Evans Lab | 2017-01-12 | 2017-01-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 105 | 105 |  | µg/L | 2 | 8 | 2017-01-18 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/L | 25.077 | 28.667 | 17.324 | 15.229 | 20.683 | 31.771
[15 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/L | 23.775 | 25.832 | 19.111 | 13.079 | 20.168 | 26.966
[15 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.002 | 0.008 | mg/L | 0.14 | 1.05 | 0.02 | 0.073 | 0.119 | 0.175
BC317-1 | EMD WWTP | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 10275 | 10275 |  | µg/L | 6 | 42 | 2017-03-23 |  | Phosphorus, total | QC 10-115-01-4-B | 0.005 | 0.035 | mg/L | 0.395 | 0.309 | 0.412 | 0.194 | 0.585 | 0.271
BC317-1 | EMD WWTP | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5562 | 5562 |  | µg/L | 2 | 8 | 2017-03-10 |  | TIN Calculated |  |  |  |  | 23.915 | 26.882 | 19.131 | 13.152 | 20.287 | 27.141
BC317-1 | EMD WWTP | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2677 | 2677 |  | µg/L | 5 | 35 | 2017-03-28
BC317-1 | EMD WWTP | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 134 | 134 |  | µg/L | 2 | 8 | 2017-03-23
BC317-2 | WJCMD WWTP | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 7597 | 7597 |  | µg/L | 6 | 42 | 2017-03-23
BC317-2 | WJCMD WWTP | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3613 | 3613 |  | µg/L | 2 | 8 | 2017-03-10
BC317-2 | WJCMD WWTP | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1995 | 1995 |  | µg/L | 5 | 35 | 2017-03-28
BC317-2 | WJCMD WWTP | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 145 | 145 |  | µg/L | 2 | 8 | 2017-03-23
BC317-3 | KSWD WWTP | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 10269 | 10269 |  | µg/L | 6 | 42 | 2017-03-23
BC317-3 | KSWD WWTP | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 8087 | 8087 |  | µg/L | 2 | 8 | 2017-03-10
BC317-3 | KSWD WWTP | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 113 | 113 |  | µg/L | 5 | 35 | 2017-03-28
BC317-3 | KSWD WWTP | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 184 | 184 |  | µg/L | 2 | 8 | 2017-03-23
BC317-4 | GWSD WWTP | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 9600 | 9600 |  | µg/L | 6 | 42 | 2017-03-23
BC317-4 | GWSD WWTP | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4280 | 4280 |  | µg/L | 2 | 8 | 2017-03-10
BC317-4 | GWSD WWTP | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4275 | 4275 |  | µg/L | 5 | 35 | 2017-03-28
BC317-4 | GWSD WWTP | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 186 | 186 |  | µg/L | 2 | 8 | 2017-03-23
BC317-5 | CSA WWTP | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 7008 | 7008 |  | µg/L | 6 | 42 | 2017-03-23
BC317-5 | CSA WWTP | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4400 | 4400 |  | µg/L | 2 | 8 | 2017-03-10
BC317-5 | CSA WWTP | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 51 | 51 |  | µg/L | 5 | 35 | 2017-03-28
BC317-5 | CSA WWTP | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 343 | 343 |  | µg/L | 2 | 8 | 2017-03-23
BC317-6 | Conifer H.S. | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 91426 | 91426 |  | µg/L | 6 | 42 | 2017-03-23
BC317-6 | Conifer H.S. | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 86674 | 86674 |  | µg/L | 2 | 8 | 2017-03-10
BC317-6 | Conifer H.S. | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 27 | 27 | J | µg/L | 5 | 35 | 2017-03-28
BC317-6 | Conifer H.S. | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 31 | 31 |  | µg/L | 2 | 8 | 2017-03-23
BC317-7 | Forest Hills WWTP | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 21407 | 21407 |  | µg/L | 6 | 42 | 2017-03-23
BC317-7 | Forest Hills WWTP | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 16185 | 16185 |  | µg/L | 2 | 8 | 2017-03-10
BC317-7 | Forest Hills WWTP | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2401 | 2401 |  | µg/L | 5 | 35 | 2017-03-28
BC317-7 | Forest Hills WWTP | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 460 | 460 |  | µg/L | 2 | 8 | 2017-03-23
BC317-8 | Morrison WWTP | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 3461 | 3461 |  | µg/L | 6 | 42 | 2017-03-23
BC317-8 | Morrison WWTP | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 151 | 151 |  | µg/L | 2 | 8 | 2017-03-10
BC317-8 | Morrison WWTP | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1124 | 1124 |  | µg/L | 5 | 35 | 2017-03-28
BC317-8 | Morrison WWTP | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 305 | 305 |  | µg/L | 2 | 8 | 2017-03-23
BC317-9 | Mt. Evans Lab | 2017-03-09 | 2017-03-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 40847 | 40847 |  | µg/L | 6 | 42 | 2017-03-23
BC317-9 | Mt. Evans Lab | 2017-03-09 | 2017-03-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 39069 | 39069 |  | µg/L | 2 | 8 | 2017-03-10
BC317-9 | Mt. Evans Lab | 2017-03-09 | 2017-03-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 39 | 39 |  | µg/L | 5 | 35 | 2017-03-28
BC317-9 | Mt. Evans Lab | 2017-03-09 | 2017-03-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 723 | 723 |  | µg/L | 2 | 8 | 2017-03-29
BC517-1 | EMD WWTP | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 9911 | 9911 |  | µg/L | 6 | 42 | 2017-05-10
BC517-1 | EMD WWTP | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9238 | 9238 |  | µg/L | 2 | 8 | 2017-05-05
BC517-1 | EMD WWTP | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 99 | 99 |  | µg/L | 5 | 35 | 2017-05-04
BC517-1 | EMD WWTP | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 230 | 230 |  | µg/L | 2 | 8 | 2017-05-10
BC517-2 | WJCMD WWTP | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 2395 | 2395 |  | µg/L | 6 | 42 | 2017-05-10
BC517-2 | WJCMD WWTP | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1084 | 1084 |  | µg/L | 2 | 8 | 2017-05-05
BC517-2 | WJCMD WWTP | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 210 | 210 |  | µg/L | 5 | 35 | 2017-05-04
BC517-2 | WJCMD WWTP | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 99 | 99 |  | µg/L | 2 | 8 | 2017-05-10
BC517-3 | KSWD WWTP | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 6953 | 6953 |  | µg/L | 6 | 42 | 2017-05-10
BC517-3 | KSWD WWTP | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4979 | 4979 |  | µg/L | 2 | 8 | 2017-05-05
BC517-3 | KSWD WWTP | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 485 | 485 |  | µg/L | 5 | 35 | 2017-05-04
BC517-3 | KSWD WWTP | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 221 | 221 |  | µg/L | 2 | 8 | 2017-05-10
BC517-4 | GWSD WWTP | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 7424 | 7424 |  | µg/L | 6 | 42 | 2017-05-10
BC517-4 | GWSD WWTP | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6702 | 6702 |  | µg/L | 2 | 8 | 2017-05-05
BC517-4 | GWSD WWTP | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 116 | 116 |  | µg/L | 5 | 35 | 2017-05-04
BC517-4 | GWSD WWTP | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 200 | 200 |  | µg/L | 2 | 8 | 2017-05-10
BC517-5 | CSA WWTP | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 8672 | 8672 |  | µg/L | 6 | 42 | 2017-05-10
BC517-5 | CSA WWTP | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5600 | 5600 |  | µg/L | 2 | 8 | 2017-05-05
BC517-5 | CSA WWTP | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 31 | 31 | J | µg/L | 5 | 35 | 2017-05-04
BC517-5 | CSA WWTP | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 771 | 771 |  | µg/L | 2 | 8 | 2017-05-10
BC517-6 | Jeffco Public Schools | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 86825 | 86825 |  | µg/L | 6 | 42 | 2017-05-19
BC517-6 | Jeffco Public Schools | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 83360 | 83360 |  | µg/L | 2 | 8 | 2017-05-18
BC517-6 | Jeffco Public Schools | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 38 | 38 |  | µg/L | 5 | 35 | 2017-05-04
BC517-6 | Jeffco Public Schools | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 71 | 71 |  | µg/L | 2 | 8 | 2017-05-10
BC517-7 | Forest Hills WWTP | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 5647 | 5647 |  | µg/L | 6 | 42 | 2017-05-10
BC517-7 | Forest Hills WWTP | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3662 | 3662 |  | µg/L | 2 | 8 | 2017-05-05
BC517-7 | Forest Hills WWTP | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 306 | 306 |  | µg/L | 5 | 35 | 2017-05-04
BC517-7 | Forest Hills WWTP | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 610 | 610 |  | µg/L | 2 | 8 | 2017-05-10
BC517-8 | Morrison WWTP | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 7054 | 7054 |  | µg/L | 6 | 42 | 2017-05-10
BC517-8 | Morrison WWTP | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 697 | 697 |  | µg/L | 2 | 8 | 2017-05-05
BC517-8 | Morrison WWTP | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4808 | 4808 |  | µg/L | 5 | 35 | 2017-05-04
BC517-8 | Morrison WWTP | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 1295 | 1295 |  | µg/L | 2 | 8 | 2017-05-10
BC517-9 | Mt. Evans Lab | 2017-05-04 | 2017-05-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 30415 | 30415 |  | µg/L | 6 | 42 | 2017-05-19
BC517-9 | Mt. Evans Lab | 2017-05-04 | 2017-05-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 28958 | 28958 |  | µg/L | 2 | 8 | 2017-05-18
BC517-9 | Mt. Evans Lab | 2017-05-04 | 2017-05-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 130 | 130 |  | µg/L | 5 | 35 | 2017-05-04
BC517-9 | Mt. Evans Lab | 2017-05-04 | 2017-05-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 224 | 224 |  | µg/L | 2 | 8 | 2017-05-10
BC717-1 | EMD WWTP | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 7004 | 7004 |  | µg/L | 6 | 42 | 2017-07-13
BC717-1 | EMD WWTP | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6411 | 6411 |  | µg/L | 2 | 8 | 2017-07-07
BC717-1 | EMD WWTP | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 58 | 58 |  | µg/L | 5 | 35 | 2017-07-26
BC717-1 | EMD WWTP | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 78 | 78 |  | µg/L | 2 | 8 | 2017-07-13
BC717-2 | WJCMD WWTP | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 2495 | 2495 |  | µg/L | 6 | 42 | 2017-07-13
BC717-2 | WJCMD WWTP | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 600 | 600 |  | µg/L | 2 | 8 | 2017-07-07
BC717-2 | WJCMD WWTP | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 579 | 579 |  | µg/L | 5 | 35 | 2017-07-26
BC717-2 | WJCMD WWTP | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 197 | 197 |  | µg/L | 2 | 8 | 2017-07-13
BC717-3 | KSWD WWTP | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 3966 | 3966 |  | µg/L | 6 | 42 | 2017-07-13
BC717-3 | KSWD WWTP | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1965 | 1965 |  | µg/L | 2 | 8 | 2017-07-07
BC717-3 | KSWD WWTP | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1013 | 1013 |  | µg/L | 5 | 35 | 2017-07-26
BC717-3 | KSWD WWTP | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 256 | 256 |  | µg/L | 2 | 8 | 2017-07-13
BC717-4 | GWSD WWTP | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 8175 | 8175 |  | µg/L | 6 | 42 | 2017-07-13
BC717-4 | GWSD WWTP | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7961 | 7961 |  | µg/L | 2 | 8 | 2017-07-07
BC717-4 | GWSD WWTP | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 91 | 91 |  | µg/L | 5 | 35 | 2017-07-26
BC717-4 | GWSD WWTP | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 358 | 358 |  | µg/L | 2 | 8 | 2017-07-13
BC717-5 | CMD WWTP | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 859 | 859 |  | µg/L | 6 | 42 | 2017-07-13
BC717-5 | CMD WWTP | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 463 | 463 |  | µg/L | 2 | 8 | 2017-07-07
BC717-5 | CMD WWTP | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 244 | 244 |  | µg/L | 5 | 35 | 2017-07-26
BC717-5 | CMD WWTP | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 21 | 21 |  | µg/L | 2 | 8 | 2017-07-13
BC717-6 | Forest Hills WWTP | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 10170 | 10170 |  | µg/L | 6 | 42 | 2017-07-20
BC717-6 | Forest Hills WWTP | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9054 | 9054 |  | µg/L | 2 | 8 | 2017-07-07
BC717-6 | Forest Hills WWTP | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 58 | 58 |  | µg/L | 5 | 35 | 2017-07-26
BC717-6 | Forest Hills WWTP | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 434 | 434 |  | µg/L | 2 | 8 | 2017-07-13
BC717-7 | Morrison WWTP | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 4050 | 4050 |  | µg/L | 6 | 42 | 2017-07-20
BC717-7 | Morrison WWTP | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1817 | 1817 |  | µg/L | 2 | 8 | 2017-07-07
BC717-7 | Morrison WWTP | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 369 | 369 |  | µg/L | 5 | 35 | 2017-07-26
BC717-7 | Morrison WWTP | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 309 | 309 |  | µg/L | 2 | 8 | 2017-07-20
BC717-8 | Mt. Evans Lab | 2017-07-06 | 2017-07-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 36273 | 36273 |  | µg/L | 6 | 42 | 2017-08-02
BC717-8 | Mt. Evans Lab | 2017-07-06 | 2017-07-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 33418 | 33418 |  | µg/L | 2 | 8 | 2017-07-28
BC717-8 | Mt. Evans Lab | 2017-07-06 | 2017-07-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 204 | 204 |  | µg/L | 5 | 35 | 2017-07-26
BC717-8 | Mt. Evans Lab | 2017-07-06 | 2017-07-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 662 | 662 |  | µg/L | 2 | 8 | 2017-07-13
BC917-1 | EMD WWTP | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 7582 | 7582 |  | µg/L | 6 | 42 | 2017-09-27
BC917-1 | EMD WWTP | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6954 | 6954 |  | µg/L | 2 | 8 | 2017-09-07
BC917-1 | EMD WWTP | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 117 | 117 |  | µg/L | 5 | 35 | 2017-09-12
BC917-1 | EMD WWTP | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 94 | 94 |  | µg/L | 2 | 8 | 2017-09-27
BC917-2 | WJCMD WWTP | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 2986 | 2986 |  | µg/L | 6 | 42 | 2017-09-27
BC917-2 | WJCMD WWTP | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1429 | 1429 |  | µg/L | 2 | 8 | 2017-09-07
BC917-2 | WJCMD WWTP | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 546 | 546 |  | µg/L | 5 | 35 | 2017-09-12
BC917-2 | WJCMD WWTP | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 196 | 196 |  | µg/L | 2 | 8 | 2017-09-27
BC917-3 | KSWD WWTP | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 3051 | 3051 |  | µg/L | 6 | 42 | 2017-09-27
BC917-3 | KSWD WWTP | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1418 | 1418 |  | µg/L | 2 | 8 | 2017-09-07
BC917-3 | KSWD WWTP | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 621 | 621 |  | µg/L | 5 | 35 | 2017-09-12
BC917-3 | KSWD WWTP | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 272 | 272 |  | µg/L | 2 | 8 | 2017-09-27
BC917-9 | GWSD WWTP | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 10930 | 10930 |  | µg/L | 6 | 42 | 2017-09-27
BC917-9 | GWSD WWTP | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9209 | 9209 |  | µg/L | 2 | 8 | 2017-09-07
BC917-9 | GWSD WWTP | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 88 | 88 |  | µg/L | 5 | 35 | 2017-09-12
BC917-9 | GWSD WWTP | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 1258 | 1258 |  | µg/L | 2 | 8 | 2017-09-27
BC917-4 | CSA WWTP | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 1799 | 1799 |  | µg/L | 6 | 42 | 2017-09-27
BC917-4 | CSA WWTP | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1011 | 1011 |  | µg/L | 2 | 8 | 2017-09-07
BC917-4 | CSA WWTP | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 46 | 46 |  | µg/L | 5 | 35 | 2017-09-12
BC917-4 | CSA WWTP | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 63 | 63 |  | µg/L | 2 | 8 | 2017-09-27
BC917-5 | JEFFCO P.S. | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 67528 | 67528 |  | µg/L | 6 | 42 | 2017-10-04
BC917-5 | JEFFCO P.S. | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 63197 | 63197 |  | µg/L | 2 | 8 | 2017-09-07
BC917-5 | JEFFCO P.S. | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 47 | 47 |  | µg/L | 5 | 35 | 2017-09-12
BC917-5 | JEFFCO P.S. | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 93 | 93 |  | µg/L | 2 | 8 | 2017-09-27
BC917-6 | Forest Hills WWTP | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 17855 | 17855 |  | µg/L | 6 | 42 | 2017-09-27
BC917-6 | Forest Hills WWTP | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 17796 | 17796 |  | µg/L | 2 | 8 | 2017-09-07
BC917-6 | Forest Hills WWTP | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 99 | 99 |  | µg/L | 5 | 35 | 2017-09-12
BC917-6 | Forest Hills WWTP | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 790 | 790 |  | µg/L | 2 | 8 | 2017-09-27
BC917-7 | Morrison WWTP | 2017-09-06 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 2317 | 2317 |  | µg/L | 6 | 42 | 2017-09-27
BC917-7 | Morrison WWTP | 2017-09-06 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1474 | 1474 |  | µg/L | 2 | 8 | 2017-09-07
BC917-7 | Morrison WWTP | 2017-09-06 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 86 | 86 |  | µg/L | 5 | 35 | 2017-09-12
BC917-7 | Morrison WWTP | 2017-09-06 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 260 | 260 |  | µg/L | 2 | 8 | 2017-09-27
BC917-8 | Mt. Evans Lab | 2017-09-07 | 2017-09-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 57949 | 57949 |  | µg/L | 6 | 42 | 2017-10-04
BC917-8 | Mt. Evans Lab | 2017-09-07 | 2017-09-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 56016 | 56016 |  | µg/L | 2 | 8 | 2017-09-07
BC917-8 | Mt. Evans Lab | 2017-09-07 | 2017-09-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 43 | 43 |  | µg/L | 5 | 35 | 2017-09-12
BC917-8 | Mt. Evans Lab | 2017-09-07 | 2017-09-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 175 | 175 |  | µg/L | 2 | 8 | 2017-09-27
BC1117-1 | EMD WWTP | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 8795 | 8795 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-1 | EMD WWTP | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5513 | 5513 |  | µg/L | 2 | 8 | 2017-11-10
BC1117-1 | EMD WWTP | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2189 | 2189 |  | µg/L | 5 | 35 | 2017-12-01
BC1117-1 | EMD WWTP | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 180 | 180 |  | µg/L | 2 | 8 | 2017-11-29
BC1117-2 | WJCMD WWTP | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 4550 | 4550 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-2 | WJCMD WWTP | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3505 | 3505 |  | µg/L | 2 | 8 | 2017-12-04
BC1117-2 | WJCMD WWTP | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 70 | 70 |  | µg/L | 5 | 35 | 2017-12-01
BC1117-2 | WJCMD WWTP | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 137 | 137 |  | µg/L | 2 | 8 | 2017-11-29
BC1117-3 | KSWD WWTP | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 5901 | 5901 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-3 | KSWD WWTP | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4541 | 4541 |  | µg/L | 2 | 8 | 2017-11-10
BC1117-3 | KSWD WWTP | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 414 | 414 |  | µg/L | 5 | 35 | 2017-12-01
BC1117-3 | KSWD WWTP | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 186 | 186 |  | µg/L | 2 | 8 | 2017-11-29
BC1117-4 | GWSD WWTP | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 8547 | 8547 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-4 | GWSD WWTP | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7912 | 7912 |  | µg/L | 2 | 8 | 2017-12-04
BC1117-4 | GWSD WWTP | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 69 | 69 |  | µg/L | 5 | 35 | 2017-12-01
BC1117-4 | GWSD WWTP | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 366 | 366 |  | µg/L | 2 | 8 | 2017-11-29
BC1117-7 | CSA | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 1778 | 1778 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-7 | CSA | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1338 | 1338 |  | µg/L | 2 | 8 | 2017-11-10
BC1117-7 | CSA | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A |  |  | U | µg/L | 5 | 35 | 2017-12-01
BC1117-7 | CSA | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 28 | 28 |  | µg/L | 2 | 8 | 2017-11-29
BC1117-5 | Conifer H.S. | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 83751 | 83751 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-5 | Conifer H.S. | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 81539 | 81539 |  | µg/L | 2 | 8 | 2017-12-04
BC1117-5 | Conifer H.S. | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 31 | 31 | J | µg/L | 5 | 35 | 2017-12-01
BC1117-5 | Conifer H.S. | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 48 | 48 |  | µg/L | 2 | 8 | 2017-11-29
BC1117-8 | Morrison | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 2454 | 2454 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-8 | Morrison | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 852 | 852 |  | µg/L | 2 | 8 | 2017-11-10
BC1117-8 | Morrison | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 160 | 160 |  | µg/L | 5 | 35 | 2017-12-01
BC1117-8 | Morrison | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 476 | 476 |  | µg/L | 2 | 8 | 2017-11-29
BC1117-6 | Mt. Evans Lab | 2017-11-09 | 2017-11-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 38717 | 38717 |  | µg/L | 6 | 42 | 2017-11-29
BC1117-6 | Mt. Evans Lab | 2017-11-09 | 2017-11-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 34284 | 34284 |  | µg/L | 2 | 8 | 2017-12-04
BC1117-6 | Mt. Evans Lab | 2017-11-09 | 2017-11-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 20 | 20 | J | µg/L | 5 | 35 | 2017-12-01
BC1117-6 | Mt. Evans Lab | 2017-11-09 | 2017-11-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 165 | 165 |  | µg/L | 2 | 8 | 2017-11-29

## Regulation 85 2018
|  | Time | Sample type | [10 empty] | WWTF | Parameter | Method | MDL | PQL | unit | 2018-01-04 | 2018-03-08 | 2018-05-10 | 2018-07-12 | 2018-09-06 | 2018-11-08 | WWTF | Parameter | Method | MDL | PQL | unit | 2018-01-04 | 2018-03-08 | 2018-05-10 | 2018-07-12 | 2018-09-06 | 2018-11-08
Evergreen Metro District | CO-0031429 | 9:00 | 12-hr | [5 empty] | 2018-01-04 |  |  |  |  | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 9919 | 13047 | 10599 | 8649 | 7230 | 12615 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 9.919 | 13.047 | 10.599 | 8.649 | 7.23 | 12.615
West Jefferson County Metro District | CO-0020915 | 9:00 | 12-hr | [5 empty] | 2018-03-08 | [5 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 7642 | 7188 | 2100 | 5096 | 5683 | 5949 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 7.642 | 7.188 | 2.1 | 5.096 | 5.683 | 5.949
Kittredge Water and Sanitation District | CO-0023841 | 9:00 | 12-hr | [5 empty] | 2018-05-10 | [5 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 222 | 5005 | 7313 | 3365 | 159 | 5460 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.222 | 5.005 | 7.313 | 3.365 | 0.159 | 5.46
Genesee Water and Sanitation District | CO-0022951 | 8:00 | 24-hr | [5 empty] | 2018-07-12 | [5 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 296 | 217 | 131 | 92 | 157 | 86 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.296 | 0.217 | 0.131 | 0.092 | 0.157 | 0.086
Forest Hills Metro District | CO-0037044 | 10:00 | 12-hr | [5 empty] | 2018-09-06 |  |  |  |  | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 5307 | 5578 | 4009 | 2776 | 12948 | 7573 |  | TIN Calculated |  |  |  | mg/l | 7.864 | 12.193 | 9.413 | 8.461 | 5.842 | 11.409
Conifer Metro District | CO-047295 | [7 empty] | 2018-11-08 | [5 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 1566 | 2133 | 1508 | 1495 | 3050 | 3540 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 5.307 | 5.578 | 4.009 | 2.776 | 12.948 | 7.573
Conifer Sanitation Association | COX-0047392 | 9:00 | grab | [11 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 2444 | 1913 | 1289 | 334 | 7298 | 2085 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 1.566 | 2.133 | 1.508 | 1.495 | 3.05 | 3.54
JCS Conifer High School | CO-047988 | 9:00 | 12-hr | [11 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 137 | 209 | 139 | 141 | 2903 | 294 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 2.444 | 1.913 | 1.289 | 0.334 | 7.298 | 2.085
Morrison | CO-0041432 | 9:00 | 12-hr | [10 empty] | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 7488 | 7638 | 7328 | 3771 | 3937 | 5821 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.137 | 0.209 | 0.139 | 0.141 | 2.903 | 0.294
Mt. Evans Lab Jeffco Schools | COG589138 | 9:00 | grab | [11 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 4615 | 5702 | 5484 | 1117 | 2289 | 3574 |  | TIN Calculated |  |  |  | mg/l | 4.01 | 4.046 | 2.797 | 1.829 | 10.348 | 5.625
[15 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 1264 | 71 | 179 | 91 | 235 | 575 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 7.488 | 7.638 | 7.328 | 3.771 | 3.937 | 5.821
24-hr WW Flows MGD | Permit | 2018-01-04 | 2018-03-08 | 2018-05-10 | 2018-07-12 | 2018-09-06 | 2018-11-08 | [7 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 295 | 382 | 197 | 561 | 315 | 181 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 4.615 | 5.702 | 5.484 | 1.117 | 2.289 | 3.574
Evergreen Metro District | CO-0031429 | 0.4 | 0.48 | 0.46 | 0.47 | 0.44 | 0.56 | [6 empty] | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 8219 | [6 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 1.264 | 0.071 | 0.179 | 0.091 | 0.235 | 0.575
West Jefferson County Metro District | CO-0020915 | 0.53 | 0.46 | 0.44 | 0.38 | 0.44 | 0.38 | [7 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 7177 | [6 empty] | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.295 | 0.382 | 0.197 | 0.561 | 0.315 | 0.181
Kittredge Water and Sanitation District | CO-0023841 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | [7 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 85 | [6 empty] | TIN Calculated |  |  |  | mg/l | 5.879 | 5.773 | 5.663 | 1.208 | 2.524 | 4.149
Forest Hills Metro District | CO-0037044 | 0.017 | 0.016 | 0.017 | 0.017 | 0.019 | 0.015 | [7 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 71 | [5 empty] | Genesee WSD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 8.219
Conifer Metro District | COX-047392 | [12 empty] | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 2738 | 1720 | 771 | 705 | 1546 | 1690 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 7.177
Conifer Sanitation Association | COG-589060 | 0.007 | 0.007 | 0.005 | 0.006 | 0.007 | 0.007 | [7 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 2235 | 1246 | 224 | 607 | 883 | 1202 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.085
JCS Conifer High School | CO-0047988 | 0.004 | 0.003 | 0.005 | 0.005 | 0.004 | 0.004 | [7 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 2458 | 44 | 29 | 27 | 43 | 16 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.071
Morrison | CO-0041432 | 0.06 | 0.08 | 0.06 | 0.13 | 0.09 | 0.05 | [7 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 29 | 2 | 4 | 10 | 22 | 47 |  | TIN Calculated |  |  |  | mg/l | 7.262
Mt. Evans Lab Jeffco Schools | COG589138 | 0.001 | 0.004 | 0.004 | 0.004 | 0.003 | 0.002 | [6 empty] | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 90922 | 77083 | 74208 |  | 47209 | 44192 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 2.738 | 1.72 | 0.771 | 0.705 | 1.546 | 1.69
[15 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 73859 | 69993 | 77404 |  | 40790 | 37674 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 2.235 | 1.246 | 0.224 | 0.607 | 0.883 | 1.202
[15 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 91 | 41 | 32 |  | 37 | 53 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 2.458 | 0.044 | 0.029 | 0.027 | 0.043 | 0.016
[15 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 63 | 95 | 92 |  | 49 | 108 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.029 | 0.002 | 0.004 | 0.01 | 0.022 | 0.047
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 26109 | 23610 | 26409 | 34144 | 33565 | 5769 |  | TIN Calculated |  |  |  | mg/l | 4.693 | 1.29 | 0.253 | 0.634 | 0.926 | 1.218
BC118-1 | EMD WWTP | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 9919 | 9919 |  | µg/L | 6 | 42 | 2018-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 22944 | 20160 | 25069 | 33943 | 28632 | 4275 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 90.922 | 77.083 | 74.208 |  | 47.209 | 44.192
BC118-1 | EMD WWTP | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7642 | 7642 |  | µg/L | 2 | 8 | 2018-01-05 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 411 | 2980 | 233 | 292 | 147 | 101 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 73.859 | 69.993 | 77.404 |  | 40.79 | 37.674
BC118-1 | EMD WWTP | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 222 | 222 |  | µg/L | 5 | 35 | 2018-02-01 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 492 | 260 | 637 | 987 | 861 | 451 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.091 | 0.041 | 0.032 |  | 0.037 | 0.053
BC118-1 | EMD WWTP | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 296 | 296 |  | µg/L | 2 | 8 | 2018-01-10 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 2983 | 2593 | 8795 | 2383 | 6743 | 1493 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.063 | 0.095 | 0.092 |  | 0.049 | 0.108
BC118-2 | WJCMD WWTP | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 5307 | 5307 |  | µg/L | 6 | 42 | 2018-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 1150 | 1548 | 902 | 1537 | 4642 | 135 | [5 empty] | mg/l | 73.95 | 70.034 | 77.436 |  | 40.827 | 37.727
BC118-2 | WJCMD WWTP | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1566 | 1566 |  | µg/L | 2 | 8 | 2018-01-05 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 120 | 98 | 5725 | 135 | 673 | 139 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 26.109 | 23.61 | 26.409 | 34.144 | 33.565 | 5.769
BC118-2 | WJCMD WWTP | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2444 | 2444 |  | µg/L | 5 | 35 | 2018-02-01 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 335 | 273 | 1101 | 125 | 190 | 170 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 22.944 | 20.16 | 25.069 | 33.943 | 28.632 | 4.275
BC118-2 | WJCMD WWTP | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 137 | 137 |  | µg/L | 2 | 8 | 2018-01-10 | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L |  | 42327 | 26884 | 28638 | 30344 | 41013 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.411 | 2.98 | 0.233 | 0.292 | 0.147 | 0.101
BC118-3 | KSWD WWTP | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 7488 | 7488 |  | µg/L | 6 | 42 | 2018-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L |  | 30013 | 26160 | 26891 | 28601 | 31226 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.492 | 0.26 | 0.637 | 0.987 | 0.861 | 0.451
BC118-3 | KSWD WWTP | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4615 | 4615 |  | µg/L | 2 | 8 | 2018-01-05 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L |  | 410 | 2328 | 4885 | 58 | 627 |  | TIN Calculated |  |  |  | mg/l | 23.355 | 23.14 | 25.302 | 34.235 | 28.779 | 4.376
BC118-3 | KSWD WWTP | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1264 | 1264 |  | µg/L | 5 | 35 | 2018-02-01 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L |  | 137 | 363 | 241 | 1005 | 361 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 2.983 | 2.593 | 8.795 | 2.383 | 6.743 | 1.493
BC118-3 | KSWD WWTP | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 295 | 295 |  | µg/L | 2 | 8 | 2018-01-10 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 1.15 | 1.548 | 0.902 | 1.537 | 4.642 | 0.135
BC118-4 | GWSD WWTP | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 8219 | 8219 |  | µg/L | 6 | 42 | 2018-01-10 | [13 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.12 | 0.098 | 5.725 | 0.135 | 0.673 | 0.139
BC118-4 | GWSD WWTP | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7177 | 7177 |  | µg/L | 2 | 8 | 2018-01-05 | [13 empty] | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.335 | 0.273 | 1.101 | 0.125 | 0.19 | 0.17
BC118-4 | GWSD WWTP | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 85 | 85 |  | µg/L | 5 | 35 | 2018-02-01 | [13 empty] | TIN Calculated |  |  |  | mg/l | 1.27 | 1.646 | 6.627 | 1.672 | 5.315 | 0.274
BC118-4 | GWSD WWTP | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 71 | 71 |  | µg/L | 2 | 8 | 2018-01-10 | [12 empty] | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l |  | 42.327 | 26.884 | 28.638 | 30.344 | 41.013
BC118-5 | CMD WWTP | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 2738 | 2738 |  | µg/L | 6 | 42 | 2018-01-10 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l |  | 30.013 | 26.16 | 26.891 | 28.601 | 31.226
BC118-5 | CMD WWTP | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2235 | 2235 |  | µg/L | 2 | 8 | 2018-01-05 | [13 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l |  | 0.41 | 2.328 | 4.885 | 0.058 | 0.627
BC118-5 | CMD WWTP | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2458 | 2458 |  | µg/L | 5 | 35 | 2018-02-01 | [13 empty] | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l |  | 0.137 | 0.363 | 0.241 | 1.005 | 0.361
BC118-5 | CMD WWTP | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 29 | 29 |  | µg/L | 2 | 8 | 2018-01-10 | [13 empty] | TIN Calculated |  |  |  | mg/l |  | 30.423 | 28.488 | 31.776 | 28.659 | 31.853
BC118-6 | Jeffco Public | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 90922 | 90922 |  | µg/L | 6 | 42 | 2018-01-10
BC118-6 | Jeffco Public | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 73859 | 73859 |  | µg/L | 2 | 8 | 2018-01-05
BC118-6 | Jeffco Public | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 91 | 91 |  | µg/L | 5 | 35 | 2018-02-01
BC118-6 | Jeffco Public | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 63 | 63 |  | µg/L | 2 | 8 | 2018-01-10
BC118-7 | Forest Hills WWTP | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 26109 | 26109 |  | µg/L | 6 | 42 | 2018-01-10 | [12 empty] | WWTF | Parameter | Method | MDL | PQL | unit | 2018-01-04 | 2018-03-08 | 2018-05-10 | 2018-07-12 | 2018-09-06 | 2018-11-08
BC118-7 | Forest Hills WWTP | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 22944 | 22944 |  | µg/L | 2 | 8 | 2018-01-05 | [12 empty] | West Jefferson MD, CO-0020915 | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 5.307 | 5.578 | 4.009 | 2.776 | 12.948 | 7.573
BC118-7 | Forest Hills WWTP | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 411 | 411 |  | µg/L | 5 | 35 | 2018-02-01 | [13 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 1.566 | 2.133 | 1.508 | 1.495 | 3.05 | 3.54
BC118-7 | Forest Hills WWTP | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 492 | 492 |  | µg/L | 2 | 8 | 2018-01-10 | [13 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 2.444 | 1.913 | 1.289 | 0.334 | 7.298 | 2.085
BC118-8 | Morrison WWTP | 2018-01-04 | 2018-01-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 2983 | 2983 |  | µg/L | 6 | 42 | 2018-01-10 | [13 empty] | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.137 | 0.209 | 0.139 | 0.141 | 2.903 | 0.294
BC118-8 | Morrison WWTP | 2018-01-04 | 2018-01-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1150 | 1150 |  | µg/L | 2 | 8 | 2018-01-05 | [13 empty] | TIN Calculated |  |  |  | mg/l | 4.01 | 4.046 | 2.797 | 1.829 | 10.348 | 5.625
BC118-8 | Morrison WWTP | 2018-01-04 | 2018-01-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 120 | 120 |  | µg/L | 5 | 35 | 2018-02-01
BC118-8 | Morrison WWTP | 2018-01-04 | 2018-01-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 335 | 335 |  | µg/L | 2 | 8 | 2018-01-10
BC318-1 | EMD WWTP | 2018-03-08 | 2018-03-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 13047 | 13047 |  | µg/L | 6 | 42 | 2018-04-03
BC318-1 | EMD WWTP | 2018-03-08 | 2018-03-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7188 | 7188 |  | µg/L | 2 | 8 | 2018-03-09
BC318-1 | EMD WWTP | 2018-03-08 | 2018-03-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 5005 | 5005 |  | µg/L | 5 | 35 | 2018-03-29
BC318-1 | EMD WWTP | 2018-03-08 | 2018-03-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 217 | 217 |  | µg/L | 2 | 8 | 2018-04-03
BC318-2 | WJCMD WWTP | 2018-03-08 | 2018-03-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 5578 | 5578 |  | µg/L | 6 | 42 | 2018-04-03
BC318-2 | WJCMD WWTP | 2018-03-08 | 2018-03-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2133 | 2133 |  | µg/L | 2 | 8 | 2018-03-09
BC318-2 | WJCMD WWTP | 2018-03-08 | 2018-03-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1913 | 1913 |  | µg/L | 5 | 35 | 2018-03-29
BC318-2 | WJCMD WWTP | 2018-03-08 | 2018-03-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 209 | 209 |  | µg/L | 2 | 8 | 2018-04-03
BC318-3 | KSWD WWTP | 2018-03-08 | 2018-03-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 7638 | 7638 |  | µg/L | 6 | 42 | 2018-04-03
BC318-3 | KSWD WWTP | 2018-03-08 | 2018-03-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5702 | 5702 |  | µg/L | 2 | 8 | 2018-03-09
BC318-3 | KSWD WWTP | 2018-03-08 | 2018-03-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 71 | 71 |  | µg/L | 5 | 35 | 2018-03-29
BC318-3 | KSWD WWTP | 2018-03-08 | 2018-03-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 382 | 382 |  | µg/L | 2 | 8 | 2018-04-03
BC318-4 | Jeffco Conifer | 2018-03-08 | 2018-03-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 77083 | 77083 |  | µg/L | 6 | 42 | 2018-04-03
BC318-4 | Jeffco Conifer | 2018-03-08 | 2018-03-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 69993 | 69993 |  | µg/L | 2 | 8 | 2018-03-09
BC318-4 | Jeffco Conifer | 2018-03-08 | 2018-03-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 41 | 41 |  | µg/L | 5 | 35 | 2018-03-29
BC318-4 | Jeffco Conifer | 2018-03-08 | 2018-03-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 95 | 95 |  | µg/L | 2 | 8 | 2018-04-03
BC318-5 | Outdoor Lab | 2018-03-08 | 2018-03-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 42327 | 42327 |  | µg/L | 6 | 42 | 2018-04-03
BC318-5 | Outdoor Lab | 2018-03-08 | 2018-03-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 30013 | 30013 |  | µg/L | 2 | 8 | 2018-03-09
BC318-5 | Outdoor Lab | 2018-03-08 | 2018-03-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 410 | 410 |  | µg/L | 5 | 35 | 2018-03-29
BC318-5 | Outdoor Lab | 2018-03-08 | 2018-03-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 137 | 137 |  | µg/L | 2 | 8 | 2018-04-03
BC318-6 | Morrison WWTP | 2018-03-08 | 2018-03-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 2593 | 2593 |  | µg/L | 6 | 42 | 2018-04-03
BC318-6 | Morrison WWTP | 2018-03-08 | 2018-03-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1548 | 1548 |  | µg/L | 2 | 8 | 2018-03-09
BC318-6 | Morrison WWTP | 2018-03-08 | 2018-03-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 98 | 98 |  | µg/L | 5 | 35 | 2018-03-29
BC318-6 | Morrison WWTP | 2018-03-08 | 2018-03-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 273 | 273 |  | µg/L | 2 | 8 | 2018-04-03
BC318-7 | CMD | 2018-03-08 | 2018-03-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1720 | 1720 |  | µg/L | 6 | 42 | 2018-04-03
BC318-7 | CMD | 2018-03-08 | 2018-03-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1246 | 1246 |  | µg/L | 2 | 8 | 2018-03-09
BC318-7 | CMD | 2018-03-08 | 2018-03-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 44 | 44 |  | µg/L | 5 | 35 | 2018-03-29
BC318-7 | CMD | 2018-03-08 | 2018-03-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 2 |  | U | µg/L | 2 | 8 | 2018-04-03
BC518B-1 | EMD WWTP | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 10599 | 10599 |  | µg/L | 6 | 42 | 2018-06-08
BC518B-1 | EMD WWTP | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2100 | 2100 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-1 | EMD WWTP | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 7313 | 7313 |  | µg/L | 5 | 35 | 2018-05-31
BC518B-1 | EMD WWTP | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 131 | 131 |  | µg/L | 2 | 8 | 2018-06-08
BC518B-2 | WJCMD WWTP | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 4009 | 4009 |  | µg/L | 6 | 42 | 2018-06-08
BC518B-2 | WJCMD WWTP | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1508 | 1508 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-2 | WJCMD WWTP | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1289 | 1289 |  | µg/L | 5 | 35 | 2018-05-31
BC518B-2 | WJCMD WWTP | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 139 | 139 |  | µg/L | 2 | 8 | 2018-06-08
BC518B-3 | KSWD WWTP | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 7328 | 7328 |  | µg/L | 6 | 42 | 2018-06-08
BC518B-3 | KSWD WWTP | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5484 | 5484 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-3 | KSWD WWTP | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 179 | 179 |  | µg/L | 5 | 35 | 2018-05-31
BC518B-3 | KSWD WWTP | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 197 | 197 |  | µg/L | 2 | 8 | 2018-06-08
BC518B-6 | Morrison WWTP | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 8795 | 8795 |  | µg/L | 6 | 42 | 2018-06-08
BC518B-6 | Morrison WWTP | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 902 | 902 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-6 | Morrison WWTP | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 5725 | 5725 |  | µg/L | 5 | 35 | 2018-05-31
BC518B-6 | Morrison WWTP | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 1101 | 1101 |  | µg/L | 2 | 8 | 2018-06-08
BC518B-4 | Forest Hills | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 26409 | 26409 |  | µg/L | 6 | 42 | 2018-06-08
BC518B-4 | Forest Hills | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 25069 | 25069 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-4 | Forest Hills | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 233 | 233 |  | µg/L | 5 | 35 | 2018-05-31
BC518B-4 | Forest Hills | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 637 | 637 |  | µg/L | 2 | 8 | 2018-06-08
BC518B-5 | Conifer Sanitation | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 771 | 771 |  | µg/L | 6 | 42 | 2018-06-08
BC518B-5 | Conifer Sanitation | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 224 | 224 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-5 | Conifer Sanitation | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 29 | 29 | J | µg/L | 5 | 35 | 2018-05-31
BC518B-5 | Conifer Sanitation | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 4 | 4 | J | µg/L | 2 | 8 | 2018-06-08
BC518B-7 | JCSD High School | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 74208 | 74208 |  | µg/L | 6 | 42 | 2018-06-21
BC518B-7 | JCSD High School | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 77404 | 77404 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-7 | JCSD High School | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 32 | 32 | J | µg/L | 5 | 35 | 2018-05-31
BC518B-7 | JCSD High School | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 92 | 92 |  | µg/L | 2 | 8 | 2018-06-08
BC518B-8 | JCSD Outdoor Lab | 2018-05-10 | 2018-05-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 26884 | 26884 |  | µg/L | 6 | 42 | 2018-06-08
BC518B-8 | JCSD Outdoor Lab | 2018-05-10 | 2018-05-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 26160 | 26160 |  | µg/L | 2 | 8 | 2018-05-11
BC518B-8 | JCSD Outdoor Lab | 2018-05-10 | 2018-05-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2328 | 2328 |  | µg/L | 5 | 35 | 2018-05-31
BC518B-8 | JCSD Outdoor Lab | 2018-05-10 | 2018-05-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 363 | 363 |  | µg/L | 2 | 8 | 2018-06-08
BC718C-1 | EVERGREEN | 2018-07-12 | 2018-07-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 8649 | 8649 |  | µg/L | 6 | 42 | 2018-08-01
BC718C-1 | EVERGREEN | 2018-07-12 | 2018-07-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5096 | 5096 |  | µg/L | 2 | 8 | 2018-07-13
BC718C-1 | EVERGREEN | 2018-07-12 | 2018-07-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 3365 | 3365 |  | µg/L | 5 | 35 | 2018-07-16
BC718C-1 | EVERGREEN | 2018-07-12 | 2018-07-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 92 | 92 |  | µg/L | 2 | 8 | 2018-07-19
BC718C-2 | WEST JEFF | 2018-07-12 | 2018-07-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 2776 | 2776 |  | µg/L | 6 | 42 | 2018-08-01
BC718C-2 | WEST JEFF | 2018-07-12 | 2018-07-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1495 | 1495 |  | µg/L | 2 | 8 | 2018-07-13
BC718C-2 | WEST JEFF | 2018-07-12 | 2018-07-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 334 | 334 |  | µg/L | 5 | 35 | 2018-07-16
BC718C-2 | WEST JEFF | 2018-07-12 | 2018-07-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 141 | 141 |  | µg/L | 2 | 8 | 2018-07-19
BC718C-3 | KITTREDGE | 2018-07-12 | 2018-07-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 3771 | 3771 |  | µg/L | 6 | 42 | 2018-08-01
BC718C-3 | KITTREDGE | 2018-07-12 | 2018-07-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1117 | 1117 |  | µg/L | 2 | 8 | 2018-07-13
BC718C-3 | KITTREDGE | 2018-07-12 | 2018-07-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 91 | 91 |  | µg/L | 5 | 35 | 2018-07-16
BC718C-3 | KITTREDGE | 2018-07-12 | 2018-07-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 561 | 561 |  | µg/L | 2 | 8 | 2018-07-19
BC718C-4 | Forest Hills | 2018-07-12 | 2018-07-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 34144 | 34144 |  | µg/L | 6 | 42 | 2018-08-01
BC718C-4 | Forest Hills | 2018-07-12 | 2018-07-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 33943 | 33943 |  | µg/L | 2 | 8 | 2018-07-13
BC718C-4 | Forest Hills | 2018-07-12 | 2018-07-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 292 | 292 |  | µg/L | 5 | 35 | 2018-07-16
BC718C-4 | Forest Hills | 2018-07-12 | 2018-07-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 987 | 987 |  | µg/L | 2 | 8 | 2018-07-19
BC718C-5 | Conifer Sanitation | 2018-07-12 | 2018-07-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 705 | 705 |  | µg/L | 6 | 42 | 2018-08-01
BC718C-5 | Conifer Sanitation | 2018-07-12 | 2018-07-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 607 | 607 |  | µg/L | 2 | 8 | 2018-07-13
BC718C-5 | Conifer Sanitation | 2018-07-12 | 2018-07-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 27 | 27 | J | µg/L | 5 | 35 | 2018-07-16
BC718C-5 | Conifer Sanitation | 2018-07-12 | 2018-07-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 10 | 10 |  | µg/L | 2 | 8 | 2018-07-19
BC718C-6 | Morrison WWTP | 2018-07-12 | 2018-07-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 2383 | 2383 |  | µg/L | 6 | 42 | 2018-08-01
BC718C-6 | Morrison WWTP | 2018-07-12 | 2018-07-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1537 | 1537 |  | µg/L | 2 | 8 | 2018-07-13
BC718C-6 | Morrison WWTP | 2018-07-12 | 2018-07-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 135 | 135 |  | µg/L | 5 | 35 | 2018-07-16
BC718C-6 | Morrison WWTP | 2018-07-12 | 2018-07-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 125 | 125 |  | µg/L | 2 | 8 | 2018-07-19
BC718C-7 | JCSD Outdoor Lab | 2018-07-12 | 2018-07-12 | Total Nitrogen | SW | QC 10-107-04-4-B | 28638 | 28638 |  | µg/L | 6 | 42 | 2018-08-01
BC718C-7 | JCSD Outdoor Lab | 2018-07-12 | 2018-07-12 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 26891 | 26891 |  | µg/L | 2 | 8 | 2018-07-13
BC718C-7 | JCSD Outdoor Lab | 2018-07-12 | 2018-07-12 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4885 | 4885 |  | µg/L | 5 | 35 | 2018-07-16
BC718C-7 | JCSD Outdoor Lab | 2018-07-12 | 2018-07-12 | Phosphorus, total | SW | QC 10-115-01-4-B | 241 | 241 |  | µg/L | 2 | 8 | 2018-07-19
BC918-1 | EVERGREEN | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 7230 | 7230 |  | µg/L | 6 | 42 | 2018-09-21
BC918-1 | EVERGREEN | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5683 | 5683 |  | µg/L | 2 | 8 | 2018-09-11
BC918-1 | EVERGREEN | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 159 | 159 |  | µg/L | 5 | 35 | 2018-09-27
BC918-1 | EVERGREEN | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 157 | 157 |  | µg/L | 2 | 8 | 2018-09-21
BC918-2 | WEST JEFF | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 12948 | 12948 |  | µg/L | 6 | 42 | 2018-09-21
BC918-2 | WEST JEFF | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3050 | 3050 |  | µg/L | 2 | 8 | 2018-09-11
BC918-2 | WEST JEFF | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 7298 | 7298 |  | µg/L | 5 | 35 | 2018-09-27
BC918-2 | WEST JEFF | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 2903 | 2903 |  | µg/L | 2 | 8 | 2018-09-21
BC918-3 | KITTREDGE | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 3937 | 3937 |  | µg/L | 6 | 42 | 2018-09-21
BC918-3 | KITTREDGE | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2289 | 2289 |  | µg/L | 2 | 8 | 2018-09-11
BC918-3 | KITTREDGE | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 235 | 235 |  | µg/L | 5 | 35 | 2018-09-27
BC918-3 | KITTREDGE | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 315 | 315 |  | µg/L | 2 | 8 | 2018-09-21
BC918-4 | Morrison WWTP | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 6743 | 6743 |  | µg/L | 6 | 42 | 2018-09-21
BC918-4 | Morrison WWTP | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4642 | 4642 |  | µg/L | 2 | 8 | 2018-09-11
BC918-4 | Morrison WWTP | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 673 | 673 |  | µg/L | 5 | 35 | 2018-09-27
BC918-4 | Morrison WWTP | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 190 | 190 |  | µg/L | 2 | 8 | 2018-09-21
BC918-5 | Forest Hills | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 33565 | 33565 |  | µg/L | 6 | 42 | 2018-09-21
BC918-5 | Forest Hills | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 28632 | 28632 |  | µg/L | 2 | 8 | 2018-09-11
BC918-5 | Forest Hills | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 147 | 147 |  | µg/L | 5 | 35 | 2018-09-27
BC918-5 | Forest Hills | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 861 | 861 |  | µg/L | 2 | 8 | 2018-09-21
BC918-6 | Conifer Sanitation | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 1546 | 1546 |  | µg/L | 6 | 42 | 2018-09-21
BC918-6 | Conifer Sanitation | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 883 | 883 |  | µg/L | 2 | 8 | 2018-09-11
BC918-6 | Conifer Sanitation | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 43 | 43 |  | µg/L | 5 | 35 | 2018-09-27
BC918-6 | Conifer Sanitation | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 22 | 22 |  | µg/L | 2 | 8 | 2018-09-21
BC918-7 | Jeffco/Conifer | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 47209 | 47209 |  | µg/L | 6 | 42 | 2018-09-21
BC918-7 | Jeffco/Conifer | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 40790 | 40790 |  | µg/L | 2 | 8 | 2018-09-11
BC918-7 | Jeffco/Conifer | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 37 | 37 |  | µg/L | 5 | 35 | 2018-09-27
BC918-7 | Jeffco/Conifer | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 49 | 49 |  | µg/L | 2 | 8 | 2018-09-21
BC918-8 | Jeffco/Mt. Evans | 2018-09-06 | 2018-09-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 30344 | 30344 |  | µg/L | 6 | 42 | 2018-09-21
BC918-8 | Jeffco/Mt. Evans | 2018-09-06 | 2018-09-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 28601 | 28601 |  | µg/L | 2 | 8 | 2018-09-11
BC918-8 | Jeffco/Mt. Evans | 2018-09-06 | 2018-09-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 58 | 58 |  | µg/L | 5 | 35 | 2018-09-27
BC918-8 | Jeffco/Mt. Evans | 2018-09-06 | 2018-09-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 1005 | 1005 |  | µg/L | 2 | 8 | 2018-09-21
BC1118B-1 | EVERGREEN | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 12615 | 12615 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-1 | EVERGREEN | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 5949 | 5949 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-1 | EVERGREEN | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 5460 | 5460 |  | µg/L | 5 | 35 | 2018-11-29
BC1118B-1 | EVERGREEN | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 86 | 86 |  | µg/L | 2 | 8 | 2018-12-06
BC1118B-2 | WEST JEFF | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 7573 | 7573 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-2 | WEST JEFF | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3540 | 3540 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-2 | WEST JEFF | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2085 | 2085 |  | µg/L | 5 | 35 | 2018-11-29
BC1118B-2 | WEST JEFF | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 294 | 294 |  | µg/L | 2 | 8 | 2018-12-06
BC1118B-3 | KITTREDGE | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 5821 | 5821 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-3 | KITTREDGE | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3574 | 3574 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-3 | KITTREDGE | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 575 | 575 |  | µg/L | 5 | 35 | 2018-11-29
BC1118B-3 | KITTREDGE | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 181 | 181 |  | µg/L | 2 | 8 | 2018-12-06
BC1118B-4 | Morrison WWTP | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1493 | 1493 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-4 | Morrison WWTP | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 135 | 135 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-4 | Morrison WWTP | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 139 | 139 |  | µg/L | 5 | 35 | 2018-11-29
BC1118B-4 | Morrison WWTP | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 170 | 170 |  | µg/L | 2 | 8 | 2018-12-06
BC1118B-5 | Forest Hills | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 5769 | 5769 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-5 | Forest Hills | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4275 | 4275 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-5 | Forest Hills | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 101 | 101 |  | µg/L | 5 | 35 | 2018-11-29
BC1118B-5 | Forest Hills | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 451 | 451 |  | µg/L | 2 | 8 | 2018-12-06
BC1118B-6 | Conifer Sanitation | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1690 | 1690 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-6 | Conifer Sanitation | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1202 | 1202 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-6 | Conifer Sanitation | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 16 | 16 | J | µg/L | 5 | 35 | 2018-11-29
BC1118B-6 | Conifer Sanitation | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 47 | 47 |  | µg/L | 2 | 8 | 2018-12-06
BC1118B-7 | JCSD High School | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 44192 | 44192 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-7 | JCSD High School | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 37674 | 37674 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-7 | JCSD High School | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 53 | 53 |  | µg/L | 5 | 35 | 2018-11-29
BC1118B-7 | JCSD High School | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 108 | 108 |  | µg/L | 2 | 8 | 2018-12-06
BC1118B-8 | JCSD Outdoor Lab | 2018-11-08 | 2018-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 41013 | 41013 |  | µg/L | 6 | 42 | 2018-12-06
BC1118B-8 | JCSD Outdoor Lab | 2018-11-08 | 2018-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 31226 | 31226 |  | µg/L | 2 | 8 | 2018-11-09
BC1118B-8 | JCSD Outdoor Lab | 2018-11-08 | 2018-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 627 | 627 |  | µg/L | 5 | 35 | 2018-11-29
BC1118B-8 | JCSD Outdoor Lab | 2018-11-08 | 2018-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 361 | 361 |  | µg/L | 2 | 8 | 2018-12-06

## Regulation 85 2019
|  | Time | Sample type |  |  |  |  | Total Nitrogen | Nitrate/Nitrite as N, dissolved | Nitrogen, ammonia | Phosphorus, total |  |  | WWTF | Parameter | Method | MDL | PQL | unit
Evergreen Metro District | CO-0031429 | 8:00 | 12-hr |  |  |  | MDL | 6 | 2 | 5 | 2 |  |  | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
West Jefferson County Metro District | CO-0020915 | 8:00 | 12-hr |  |  |  | PQL | 42 | 8 | 35 | 8 |  |  |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
Kittredge Water and Sanitation District | CO-0023841 | 8:00 | 12-hr |  |  |  | Method | QC 10-107-04-4-B | QC 10-107-04-1-C | QC 10-107-06-2-A | QC 10-115-01-4-B |  |  |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
Forest Hills Metro District | CO-0037044 | 8:00 | 12-hr | [11 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
Conifer Sanitation Association | COX-0047392 | 6:00 | grab | [10 empty] | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
JCS Conifer High School | CO-047988 | 10:30 | 12-hr | [11 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
Morrison | CO-0041432 | 9:00 | 12-hr | [11 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
Mt. Evans Lab Jeffco Schools | COG589138 | 10:00 | grab | [11 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
|  | 24-hr Effluent Flows | [11 empty] | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
24-hr WW Flows MGD | Permit | 2019-01-04 | 2019-03-06 | 2019-05-08 | 2019-07-10 | 2019-09-04 | 2019-11-07 |  | 1/4/19: 9,852 gallons |  | 0.009852 |  |  |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
Evergreen Metro District | CO-0031429 | 0.4762 | 0.5770 | 0.4740 | 0.4339 | 0.4264 | 0.4327 |  | 3/6/19: 0 |  | 0.0070575 |  |  |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
West Jefferson County Metro District | CO-0020915 | 0.4083 | 0.3992 | 0.4677 | 0.4834 | 0.4116 | 0.4838 |  | 5/8/19: 4,163 |  | 0.004163 |  |  |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
Kittredge Water and Sanitation District | CO-0023841 | 0.0455 | 0.0514 | 0.0604 | 0.0416 | 0.0476 | 0.0383 |  | 7/10/19: 3,164 |  | 0.003164 |  |  | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
Forest Hills Metro District | CO-0037044 | 0.017152 | 0.019256 | 0.025077 | 0.019284 | 0.019284 | 0.020107 |  | 9/4/19: 3,687 |  | 0.003687 |  |  |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
Conifer Sanitation Association | COG-589060 | 0.0099 | 0.0071 | 0.0042 | 0.0032 | 0.0037 | 0.0025 |  | 11/7/19: 2,496 |  | 0.002496 |  |  |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
JCS Conifer High School | CO-0047988 | 0.0072 | .0097 | .0064 | 0 | .0061 | .0079 | [7 empty] | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
Morrison | CO-0041432 | 0.059848 | 0.051432 | 0.082408 | 0.081024 | 0.084096 | 0.090272 | [6 empty] | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
Mt. Evans Lab Jeffco Schools | COG589138 | .00059 | .00249 | .00376 | .00494 | .00189 | .00236 | [7 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
[15 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
LABID | CLIENTID | COLLECTDATE | RECEIVEDATE | ANALYTE | MATRIX | METHOD | RESULT | RESULT | QUAL | UNITS | MDL | PQL | ANALYZEDATE |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
BC119B-1 | EVERGREEN | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 10709 | 10709 |  | µg/L | 6 | 42 | 2019-01-23 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
BC119B-1 | EVERGREEN | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6614 | 6614 |  | µg/L | 2 | 8 | 2019-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
BC119B-1 | EVERGREEN | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2649 | 2649 |  | µg/L | 5 | 35 | 2019-01-30 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
BC119B-1 | EVERGREEN | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 260 | 260 |  | µg/L | 2 | 8 | 2019-01-23 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
BC119B-2 | WEST JEFF | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 5971 | 5971 |  | µg/L | 6 | 42 | 2019-01-23 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
BC119B-2 | WEST JEFF | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3174 | 3174 |  | µg/L | 2 | 8 | 2019-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
BC119B-2 | WEST JEFF | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 989 | 989 |  | µg/L | 5 | 35 | 2019-01-30 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
BC119B-2 | WEST JEFF | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 166 | 166 |  | µg/L | 2 | 8 | 2019-01-23 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
BC119B-3 | KITTREDGE | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 6170 | 6170 |  | µg/L | 6 | 42 | 2019-01-23 | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L
BC119B-3 | KITTREDGE | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4287 | 4287 |  | µg/L | 2 | 8 | 2019-01-10 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L
BC119B-3 | KITTREDGE | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 519 | 519 |  | µg/L | 5 | 35 | 2019-01-30 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L
BC119B-3 | KITTREDGE | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 100 | 100 |  | µg/L | 2 | 8 | 2019-01-23 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L
BC119B-4 | Morrison WWTP | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 4951 | 4951 |  | µg/L | 6 | 42 | 2019-01-23
BC119B-4 | Morrison WWTP | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 368 | 368 |  | µg/L | 2 | 8 | 2019-01-10 | WWTF | Parameter | Method | MDL | PQL | unit | 2019-01-04 | 2019-03-06 | 2019-05-08 | 2019-07-10 | 2019-09-04 | 2019-11-07
BC119B-4 | Morrison WWTP | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 2829 | 2829 |  | µg/L | 5 | 35 | 2019-01-30 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 10709 | 1264 | 13112 | 5141 | 7489 | 11342
BC119B-4 | Morrison WWTP | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 243 | 243 |  | µg/L | 2 | 8 | 2019-01-23 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 6614 | 672 | 6745 | 4450 | 4955 | 7854
BC119B-5 | Forest Hills | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 24394 | 24394 |  | µg/L | 6 | 42 | 2019-01-23 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 2649 | 130 | 4856 | 302 | 1842 | 54
BC119B-5 | Forest Hills | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 20233 | 20233 |  | µg/L | 2 | 8 | 2019-01-10 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 260 | 13 | 173 | 315 | 211 | 306
BC119B-5 | Forest Hills | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 367 | 367 |  | µg/L | 5 | 35 | 2019-01-30 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 5971 | 1264 | 3643 | 2053 | 4774 | 3686
BC119B-5 | Forest Hills | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 435 | 435 |  | µg/L | 2 | 8 | 2019-01-23 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 3174 | 672 | 2564 | 423 | 323 | 841
BC119B-6 | Conifer Sanitation | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 1264 | 1264 |  | µg/L | 6 | 42 | 2019-01-23 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 989 | 130 | 91 | 589 | 3789 | 1733
BC119B-6 | Conifer Sanitation | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 672 | 672 |  | µg/L | 2 | 8 | 2019-01-10 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 166 | 13 | 94 | 234 | 271 | 141
BC119B-6 | Conifer Sanitation | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 130 | 130 |  | µg/L | 5 | 35 | 2019-01-30 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 6170 | 1264 | 9674 | 11889 | 5231 | 5922
BC119B-6 | Conifer Sanitation | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 13 | 13 |  | µg/L | 2 | 8 | 2019-01-23 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 4287 | 672 | 683 | 9628 | 3828 | 4384
BC119B-7 | JCSD High School | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 64730 | 64730 |  | µg/L | 6 | 42 | 2019-01-23 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 519 | 130 | 9527 | 226 | 269 | 221
BC119B-7 | JCSD High School | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 57760 | 57760 |  | µg/L | 2 | 8 | 2019-01-10 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 100 | 13 | 592 | 579 | 475 | 196
BC119B-7 | JCSD High School | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 124 | 124 |  | µg/L | 5 | 35 | 2019-01-30 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 1264 | 2266 | 1353 | 1738 | 1020 | 1837
BC119B-7 | JCSD High School | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 60 | 60 |  | µg/L | 2 | 8 | 2019-01-23 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 672 | 1727 | 743 | 1132 | 282 | 1273
BC119B-8 | JCSD Outdoor Lab | 2019-01-09 | 2019-01-09 | Total Nitrogen | SW | QC 10-107-04-4-B | 30367 | 30367 |  | µg/L | 6 | 42 | 2019-01-23 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 130 | 129 | 119 | 96 | 96 | 71
BC119B-8 | JCSD Outdoor Lab | 2019-01-09 | 2019-01-09 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 30115 | 30115 |  | µg/L | 2 | 8 | 2019-01-10 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 13 | 59 | 6 | 6 | 6 | 45
BC119B-8 | JCSD Outdoor Lab | 2019-01-09 | 2019-01-09 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 176 | 176 |  | µg/L | 5 | 35 | 2019-01-30 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 64730 | 91145 | 80087 |  | 37706 | 29995
BC119B-8 | JCSD Outdoor Lab | 2019-01-09 | 2019-01-09 | Phosphorus, total | SW | QC 10-115-01-4-B | 877 | 877 |  | µg/L | 2 | 8 | 2019-01-23 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 57760 | 67520 | 56151 |  | 35898 | 9604
[15 empty] | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 124 | 110 | 89 |  | 286 | 20997
BC319-1 | EMD | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 1264 | 7885 |  | µg/L | 6 | 42 | 2019-03-20 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 60 | 72 | 48 |  | 266 | 99
BC319-1 | EMD | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 672 | 3867 |  | µg/L | 2 | 8 | 2019-03-07 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 24394 | 26325 | 23743 | 26985 | 10250 | 23500
BC319-1 | EMD | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 130 | 3133 |  | µg/L | 5 | 35 | 2019-03-28 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 20233 | 21982 | 18474 | 23953 | 9698 | 20649
BC319-1 | EMD | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 13 | 393 |  | µg/L | 2 | 8 | 2019-03-20 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 367 | 201 | 163 | 111 | 107 | 309
BC319-2 | WJCMD | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 1264 | 8247 |  | µg/L | 6 | 42 | 2019-03-20 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 435 | 524 | 721 | 540 | 284 | 145
BC319-2 | WJCMD | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 672 | 6742 |  | µg/L | 2 | 8 | 2019-03-07 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 4951 | 2664 | 4728 | 2232 | 1560 | 8167
BC319-2 | WJCMD | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 130 | 171 |  | µg/L | 5 | 35 | 2019-03-28 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 368 | 316 | 1935 | 1055 | 434 | 2337
BC319-2 | WJCMD | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 13 | 196 |  | µg/L | 2 | 8 | 2019-03-20 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 2829 | 1086 | 1646 | 279 | 225 | 4346
BC319-3 | KSWD | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 1264 | 12727 |  | µg/L | 6 | 42 | 2019-03-20 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 243 | 151 | 291 | 206 | 156 | 206
BC319-3 | KSWD | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 672 | 10279 |  | µg/L | 2 | 8 | 2019-03-07 | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 6 | 42 | µg/L | 30367 | 36137 | 38369 | 30929 | 41623 | 38758
BC319-3 | KSWD | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 130 | 241 |  | µg/L | 5 | 35 | 2019-03-28 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 2 | 8 | µg/L | 30115 | 27241 | 28073 | 9786 | 38401 | 36919
BC319-3 | KSWD | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 13 | 403 |  | µg/L | 2 | 8 | 2019-03-20 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 5 | 35 | µg/L | 176 | 5695 | 1456 | 23003 | 5323 | 46
BC319-4 | Conifer Metro | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 2266 | 2266 |  | µg/L | 6 | 42 | 2019-03-20 |  | Phosphorus, total | QC 10-115-01-4-B | 2 | 8 | µg/L | 877 | 585 | 779 | 605 | 102 | 276
BC319-4 | Conifer Metro | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1727 | 1727 |  | µg/L | 2 | 8 | 2019-03-07
BC319-4 | Conifer Metro | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 129 | 129 |  | µg/L | 5 | 35 | 2019-03-28 | WWTF | Parameter | Method | MDL | ML | unit | 2019-01-04 | 2019-03-06 | 2019-05-08 | 2019-07-10 | 2019-09-04 | 2019-11-07
BC319-4 | Conifer Metro | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 59 | 59 |  | µg/L | 2 | 8 | 2019-03-20 | Evergreen MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 10.709 | 1.264 | 13.112 | 5.141 | 7.489 | 11.342
BC319-5 | Jeffco/Conifer | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 91145 | 91145 |  | µg/L | 6 | 42 | 2019-03-20 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 6.614 | 0.672 | 6.745 | 4.45 | 4.955 | 7.854
BC319-5 | Jeffco/Conifer | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 67520 | 67520 |  | µg/L | 2 | 8 | 2019-03-07 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 2.649 | 0.13 | 4.856 | 0.302 | 1.842 | 0.054
BC319-5 | Jeffco/Conifer | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 110 | 110 |  | µg/L | 5 | 35 | 2019-03-28 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.26 | 0.013 | 0.173 | 0.315 | 0.211 | 0.306
[15 empty] | TIN Calculated | Calcualte | 0.005 | 0.035 | mg/l | 9.263 | 0.802 | 11.601 | 4.752 | 6.797 | 7.908
BC319-5 | Jeffco/Conifer | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 72 | 72 |  | µg/L | 2 | 8 | 2019-03-20 | West Jefferson MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 5.971 | 1.264 | 3.643 | 2.053 | 4.774 | 3.686
BC319-6 | Forest Hills | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 26325 | 26325 |  | µg/L | 6 | 42 | 2019-03-20 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 3.174 | 0.672 | 2.564 | 0.423 | 0.323 | 0.841
BC319-6 | Forest Hills | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 21982 | 21982 |  | µg/L | 2 | 8 | 2019-03-07 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.989 | 0.13 | 0.091 | 0.589 | 3.789 | 1.733
BC319-6 | Forest Hills | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 201 | 201 |  | µg/L | 5 | 35 | 2019-03-28 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.166 | 0.013 | 0.094 | 0.234 | 0.271 | 0.141
[15 empty] | TIN Calculated |  |  |  | mg/l | 4.163 | 0.802 | 2.655 | 1.012 | 4.112 | 2.574
BC319-6 | Forest Hills | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 524 | 524 |  | µg/L | 2 | 8 | 2019-03-20 | Kittredge SWD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 6.17 | 1.264 | 9.674 | 11.889 | 5.231 | 5.922
BC319-7 | Morrison | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 2664 | 2664 |  | µg/L | 6 | 42 | 2019-03-20 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 4.287 | 0.672 | 0.683 | 9.628 | 3.828 | 4.384
BC319-7 | Morrison | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 316 | 316 |  | µg/L | 2 | 8 | 2019-03-07 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.519 | 0.13 | 9.527 | 0.226 | 0.269 | 0.221
BC319-7 | Morrison | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1086 | 1086 |  | µg/L | 5 | 35 | 2019-03-28 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.1 | 0.013 | 0.592 | 0.579 | 0.475 | 0.196
[15 empty] | TIN Calculated |  |  |  | mg/l | 4.806 | 0.802 | 10.21 | 9.854 | 4.097 | 4.605
BC319-7 | Morrison | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 151 | 151 |  | µg/L | 2 | 8 | 2019-03-20 | Conifer Sanitation Association | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 1.264 | 2.266 | 1.353 | 1.738 | 1.02 | 1.837
BC319-8 | Jeffco/Mt. Evans | 2019-03-06 | 2019-03-06 | Total Nitrogen | SW | QC 10-107-04-4-B | 36137 | 36137 |  | µg/L | 6 | 42 | 2019-03-20 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 0.672 | 1.727 | 0.743 | 1.132 | 0.282 | 1.273
BC319-8 | Jeffco/Mt. Evans | 2019-03-06 | 2019-03-06 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 27241 | 27241 |  | µg/L | 2 | 8 | 2019-03-07 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.13 | 0.129 | 0.119 | 0.096 | 0.096 | 0.071
BC319-8 | Jeffco/Mt. Evans | 2019-03-06 | 2019-03-06 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 5695 | 5695 |  | µg/L | 5 | 35 | 2019-03-28 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.013 | 0.059 | 0.006 | 0.006 | 0.006 | 0.045
[15 empty] | TIN Calculated |  |  |  | mg/l | 0.802 | 1.856 | 0.862 | 1.228 | 0.378 | 1.344
BC319-8 | Jeffco/Mt. Evans | 2019-03-06 | 2019-03-06 | Phosphorus, total | SW | QC 10-115-01-4-B | 585 | 585 |  | µg/L | 2 | 8 | 2019-03-20 | JCS High School | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 64.73 | 91.145 | 80.087 | 0 | 37.706 | 29.995
[15 empty] | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 57.76 | 67.52 | 56.151 | 0 | 35.898 | 9.604
BC519B-1 | Evergreen | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 13112 | 13112 |  | µg/L | 26 | 104 | 2019-05-16 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.124 | 0.11 | 0.089 | 0 | 0.286 | 20.997
BC519B-1 | Evergreen | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 6745 | 6745 |  | µg/L | 6 | 24 | 2019-05-09 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.06 | 0.072 | 0.048 | 0 | 0.266 | 0.099
[15 empty] | TIN Calculated |  |  |  | mg/l | 57.884 | 67.63 | 56.24 | 0 | 36.184 | 30.601
BC519B-1 | Evergreen | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4856 | 4856 |  | µg/L | 10 | 40 | 2019-05-22 | Forest Hills MD | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 24.394 | 26.325 | 23.743 | 26.985 | 10.25 | 23.5
BC519B-1 | Evergreen | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 173 | 173 |  | µg/L | 6 | 24 | 2019-05-24 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 20.233 | 21.982 | 18.474 | 23.953 | 9.698 | 20.649
BC519B-2 | West Jeff | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 3643 | 3643 |  | µg/L | 26 | 104 | 2019-05-16 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.367 | 0.201 | 0.163 | 0.111 | 0.107 | 0.309
BC519B-2 | West Jeff | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2564 | 2564 |  | µg/L | 6 | 24 | 2019-05-09 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.435 | 0.524 | 0.721 | 0.54 | 0.284 | 0.145
[15 empty] | TIN Calculated |  |  |  | mg/l | 20.6 | 22.183 | 18.637 | 24.064 | 9.805 | 20.958
BC519B-2 | West Jeff | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 91 | 91 |  | µg/L | 10 | 40 | 2019-05-22 | Morrison | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 4.951 | 2.664 | 4.728 | 2.232 | 1.56 | 8.167
BC519B-2 | West Jeff | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 94 | 94 |  | µg/L | 6 | 24 | 2019-05-16 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 0.368 | 0.316 | 1.935 | 1.055 | 0.434 | 2.337
BC519B-3 | Kittredge | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 9674 | 9674 |  | µg/L | 26 | 104 | 2019-05-16 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 2.829 | 1.086 | 1.646 | 0.279 | 0.225 | 4.346
BC519B-3 | Kittredge | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 683 | 683 |  | µg/L | 6 | 24 | 2019-05-09 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.243 | 0.151 | 0.291 | 0.206 | 0.156 | 0.206
[15 empty] | TIN Calculated |  |  |  | mg/l | 3.197 | 1.402 | 3.581 | 1.334 | 0.659 | 6.683
BC519B-3 | Kittredge | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 9527 | 9527 |  | µg/L | 10 | 40 | 2019-05-22 | Mt. Evans Lab Jeffco Schools | Total Nitrogen | QC 10-107-04-4-B | 0.006 | 0.042 | mg/l | 30.367 | 36.137 | 38.369 | 30.929 | 41.623 | 38.758
BC519B-3 | Kittredge | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 592 | 592 |  | µg/L | 6 | 24 | 2019-05-16 |  | Nitrate/Nitrite as N, dissolved | QC 10-107-04-1-C | 0.002 | 0.008 | mg/l | 30.115 | 27.241 | 28.073 | 9.786 | 38.401 | 36.919
BC519B-6 | Conifer Station | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 1353 | 1353 |  | µg/L | 26 | 104 | 2019-05-16 |  | Nitrogen, ammonia | QC 10-107-06-2-A | 0.005 | 0.035 | mg/l | 0.176 | 5.695 | 1.456 | 23.003 | 5.323 | 0.046
BC519B-6 | Conifer Station | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 743 | 743 |  | µg/L | 6 | 24 | 2019-05-09 |  | Phosphorus, total | QC 10-115-01-4-B | 0.002 | 0.008 | mg/l | 0.877 | 0.585 | 0.779 | 0.605 | 0.102 | 0.276
BC519B-6 | Conifer Station | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 119 | 119 |  | µg/L | 10 | 40 | 2019-05-22 |  | TIN Calculated |  |  |  | mg/l | 30.291 | 32.936 | 29.529 | 32.789 | 43.724 | 36.965
BC519B-6 | Conifer Station | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 6 |  | U | µg/L | 6 | 24 | 2019-05-16
BC519B-7 | JCSD High School | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 80087 | 80087 |  | µg/L | 26 | 104 | 2019-05-16
BC519B-7 | JCSD High School | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 56151 | 56151 |  | µg/L | 6 | 24 | 2019-05-09
BC519B-7 | JCSD High School | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 89 | 89 |  | µg/L | 10 | 40 | 2019-05-22
BC519B-7 | JCSD High School | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 48 | 48 |  | µg/L | 6 | 24 | 2019-05-24
BC519B-5 | Forest Hills | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 23743 | 23743 |  | µg/L | 26 | 104 | 2019-05-16
BC519B-5 | Forest Hills | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 18474 | 18474 |  | µg/L | 6 | 24 | 2019-05-09
BC519B-5 | Forest Hills | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 163 | 163 |  | µg/L | 10 | 40 | 2019-05-22
BC519B-5 | Forest Hills | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 721 | 721 |  | µg/L | 6 | 24 | 2019-05-24
BC519B-4 | Morrison | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 4728 | 4728 |  | µg/L | 26 | 104 | 2019-05-16
BC519B-4 | Morrison | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1935 | 1935 |  | µg/L | 6 | 24 | 2019-05-09
BC519B-4 | Morrison | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1646 | 1646 |  | µg/L | 10 | 40 | 2019-05-22
BC519B-4 | Morrison | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 291 | 291 |  | µg/L | 6 | 24 | 2019-05-16
BC519B-8 | JCSD Outdoor Lab | 2019-05-08 | 2019-05-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 38369 | 38369 |  | µg/L | 26 | 104 | 2019-05-16
BC519B-8 | JCSD Outdoor Lab | 2019-05-08 | 2019-05-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 28073 | 28073 |  | µg/L | 6 | 24 | 2019-05-09
BC519B-8 | JCSD Outdoor Lab | 2019-05-08 | 2019-05-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1456 | 1456 |  | µg/L | 10 | 40 | 2019-05-22
BC519B-8 | JCSD Outdoor Lab | 2019-05-08 | 2019-05-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 779 | 779 |  | µg/L | 6 | 24 | 2019-05-24
BC719C-1 | Evergreen | 2019-07-10 | 2019-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 5141 | 5141 |  | µg/L | 26 | 104 | 2019-07-25
BC719C-1 | Evergreen | 2019-07-10 | 2019-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4450 | 4450 |  | µg/L | 6 | 24 | 2019-07-11
BC719C-1 | Evergreen | 2019-07-10 | 2019-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 302 | 302 |  | µg/L | 10 | 40 | 2019-07-30
BC719C-1 | Evergreen | 2019-07-10 | 2019-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 315 | 315 |  | µg/L | 6 | 24 | 2019-08-02
BC719C-2 | West Jeff | 2019-07-10 | 2019-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 2053 | 2053 |  | µg/L | 26 | 104 | 2019-07-25
BC719C-2 | West Jeff | 2019-07-10 | 2019-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 423 | 423 |  | µg/L | 6 | 24 | 2019-07-11
BC719C-2 | West Jeff | 2019-07-10 | 2019-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 589 | 589 |  | µg/L | 10 | 40 | 2019-07-30
BC719C-2 | West Jeff | 2019-07-10 | 2019-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 234 | 234 |  | µg/L | 6 | 24 | 2019-07-25
BC719C-3 | Kittredge | 2019-07-10 | 2019-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 11889 | 11889 |  | µg/L | 26 | 104 | 2019-07-25
BC719C-3 | Kittredge | 2019-07-10 | 2019-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9628 | 9628 |  | µg/L | 6 | 24 | 2019-07-11
BC719C-3 | Kittredge | 2019-07-10 | 2019-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 226 | 226 |  | µg/L | 10 | 40 | 2019-07-30
BC719C-3 | Kittredge | 2019-07-10 | 2019-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 579 | 579 |  | µg/L | 6 | 24 | 2019-08-02
BC719C-6 | Conifer Station | 2019-07-10 | 2019-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 1738 | 1738 |  | µg/L | 26 | 104 | 2019-07-25
BC719C-6 | Conifer Station | 2019-07-10 | 2019-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1132 | 1132 |  | µg/L | 6 | 24 | 2019-07-11
BC719C-6 | Conifer Station | 2019-07-10 | 2019-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 96 | 96 |  | µg/L | 10 | 40 | 2019-07-30
BC719C-6 | Conifer Station | 2019-07-10 | 2019-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 6 |  | U | µg/L | 6 | 24 | 2019-07-25
BC719C-7 | Forest Hills | 2019-07-10 | 2019-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 26985 | 26985 |  | µg/L | 26 | 104 | 2019-07-25
BC719C-7 | Forest Hills | 2019-07-10 | 2019-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 23953 | 23953 |  | µg/L | 6 | 24 | 2019-07-11
BC719C-7 | Forest Hills | 2019-07-10 | 2019-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 111 | 111 |  | µg/L | 10 | 40 | 2019-07-30
BC719C-7 | Forest Hills | 2019-07-10 | 2019-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 540 | 540 |  | µg/L | 6 | 24 | 2019-08-02
BC719C-5 | Morrison | 2019-07-10 | 2019-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 2232 | 2232 |  | µg/L | 26 | 104 | 2019-07-25
BC719C-5 | Morrison | 2019-07-10 | 2019-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1055 | 1055 |  | µg/L | 6 | 24 | 2019-07-11
BC719C-5 | Morrison | 2019-07-10 | 2019-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 279 | 279 |  | µg/L | 10 | 40 | 2019-07-30
BC719C-5 | Morrison | 2019-07-10 | 2019-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 206 | 206 |  | µg/L | 6 | 24 | 2019-07-25
BC719C-4 | JCSD Outdoor Lab | 2019-07-10 | 2019-07-10 | Total Nitrogen | SW | QC 10-107-04-4-B | 30929 | 30929 |  | µg/L | 26 | 104 | 2019-07-25
BC719C-4 | JCSD Outdoor Lab | 2019-07-10 | 2019-07-10 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9786 | 9786 |  | µg/L | 6 | 24 | 2019-07-11
BC719C-4 | JCSD Outdoor Lab | 2019-07-10 | 2019-07-10 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 23003 | 23003 |  | µg/L | 10 | 40 | 2019-07-30
BC719C-4 | JCSD Outdoor Lab | 2019-07-10 | 2019-07-10 | Phosphorus, total | SW | QC 10-115-01-4-B | 605 | 605 |  | µg/L | 6 | 24 | 2019-08-02
BC919-1 | Evergreen | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 7489 | 7489 |  | µg/L | 26 | 104 | 2019-10-03
BC919-1 | Evergreen | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4955 | 4955 |  | µg/L | 6 | 24 | 2019-09-04
BC919-1 | Evergreen | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1842 | 1842 |  | µg/L | 10 | 40 | 2019-10-01
BC919-1 | Evergreen | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 211 | 211 |  | µg/L | 6 | 24 | 2019-10-03
BC919-2 | West Jeff | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 4774 | 4774 |  | µg/L | 26 | 104 | 2019-10-03
BC919-2 | West Jeff | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 323 | 323 |  | µg/L | 6 | 24 | 2019-09-04
BC919-2 | West Jeff | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 3789 | 3789 |  | µg/L | 10 | 40 | 2019-10-01
BC919-2 | West Jeff | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 271 | 271 |  | µg/L | 6 | 24 | 2019-10-03
BC919-3 | Kittredge | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 5231 | 5231 |  | µg/L | 26 | 104 | 2019-10-03
BC919-3 | Kittredge | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 3828 | 3828 |  | µg/L | 6 | 24 | 2019-09-04
BC919-3 | Kittredge | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 269 | 269 |  | µg/L | 10 | 40 | 2019-10-01
BC919-3 | Kittredge | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 475 | 475 |  | µg/L | 6 | 24 | 2019-10-03
BC919-6 | Conifer Station | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 1020 | 1020 |  | µg/L | 26 | 104 | 2019-10-03
BC919-6 | Conifer Station | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 282 | 282 |  | µg/L | 6 | 24 | 2019-09-04
BC919-6 | Conifer Station | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 96 | 96 |  | µg/L | 10 | 40 | 2019-10-01
BC919-6 | Conifer Station | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 6 | 6 | J | µg/L | 6 | 24 | 2019-10-03
BC919-7 | JCSD High School | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 37706 | 37706 |  | µg/L | 26 | 104 | 2019-10-03
BC919-7 | JCSD High School | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 35898 | 35898 |  | µg/L | 6 | 24 | 2019-09-04
BC919-7 | JCSD High School | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 286 | 286 |  | µg/L | 10 | 40 | 2019-10-01
BC919-7 | JCSD High School | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 266 | 266 |  | µg/L | 6 | 24 | 2019-10-03
BC919-5 | Forest Hills | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 10250 | 10250 |  | µg/L | 26 | 104 | 2019-10-03
BC919-5 | Forest Hills | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9698 | 9698 |  | µg/L | 6 | 24 | 2019-09-04
BC919-5 | Forest Hills | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 107 | 107 |  | µg/L | 10 | 40 | 2019-10-01
BC919-5 | Forest Hills | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 284 | 284 |  | µg/L | 6 | 24 | 2019-10-03
BC919-4 | Morrison | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 1560 | 1560 |  | µg/L | 26 | 104 | 2019-10-03
BC919-4 | Morrison | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 434 | 434 |  | µg/L | 6 | 24 | 2019-09-04
BC919-4 | Morrison | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 225 | 225 |  | µg/L | 10 | 40 | 2019-10-01
BC919-4 | Morrison | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 156 | 156 |  | µg/L | 6 | 24 | 2019-10-03
BC919-8 | JCSD Outdoor Lab | 2019-09-04 | 2019-09-04 | Total Nitrogen | SW | QC 10-107-04-4-B | 41623 | 41623 |  | µg/L | 26 | 104 | 2019-10-03
BC919-8 | JCSD Outdoor Lab | 2019-09-04 | 2019-09-04 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 38401 | 38401 |  | µg/L | 6 | 24 | 2019-09-04
BC919-8 | JCSD Outdoor Lab | 2019-09-04 | 2019-09-04 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 5323 | 5323 |  | µg/L | 10 | 40 | 2019-10-01
BC919-8 | JCSD Outdoor Lab | 2019-09-04 | 2019-09-04 | Phosphorus, total | SW | QC 10-115-01-4-B | 102 | 102 |  | µg/L | 6 | 24 | 2019-10-03
BC1119-1 | EMD WWTP | 2019-11-07 | 2019-11-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 11342 | 11342 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-1 | EMD WWTP | 2019-11-07 | 2019-11-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 7854 | 7854 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-1 | EMD WWTP | 2019-11-07 | 2019-11-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 54 | 54 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-1 | EMD WWTP | 2019-11-07 | 2019-11-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 306 | 306 |  | µg/L | 6 | 24 | 2019-11-15
BC1119-2 | WJCMD WWTP | 2019-11-07 | 2019-11-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 3686 | 3686 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-2 | WJCMD WWTP | 2019-11-07 | 2019-11-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 841 | 841 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-2 | WJCMD WWTP | 2019-11-07 | 2019-11-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 1733 | 1733 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-2 | WJCMD WWTP | 2019-11-07 | 2019-11-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 141 | 141 |  | µg/L | 6 | 24 | 2019-11-15
BC1119-3 | KSWD WWTP | 2019-11-07 | 2019-11-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 5922 | 5922 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-3 | KSWD WWTP | 2019-11-07 | 2019-11-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 4384 | 4384 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-3 | KSWD WWTP | 2019-11-07 | 2019-11-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 221 | 221 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-3 | KSWD WWTP | 2019-11-07 | 2019-11-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 196 | 196 |  | µg/L | 6 | 24 | 2019-11-15
BC1119-5 | CMD WWTP | 2019-11-07 | 2019-11-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 1837 | 1837 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-5 | CMD WWTP | 2019-11-07 | 2019-11-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 1273 | 1273 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-5 | CMD WWTP | 2019-11-07 | 2019-11-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 71 | 71 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-5 | CMD WWTP | 2019-11-07 | 2019-11-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 45 | 45 |  | µg/L | 6 | 24 | 2019-11-15
BC1119-7 | Conifer High School | 2019-11-07 | 2019-11-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 29995 | 29995 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-7 | Conifer High School | 2019-11-07 | 2019-11-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 9604 | 9604 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-7 | Conifer High School | 2019-11-07 | 2019-11-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 20997 | 20997 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-7 | Conifer High School | 2019-11-07 | 2019-11-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 99 | 99 |  | µg/L | 6 | 24 | 2019-11-15
BC1119-6 | Forest Hills WWTP | 2019-11-07 | 2019-11-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 23500 | 23500 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-6 | Forest Hills WWTP | 2019-11-07 | 2019-11-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 20649 | 20649 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-6 | Forest Hills WWTP | 2019-11-07 | 2019-11-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 309 | 309 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-6 | Forest Hills WWTP | 2019-11-07 | 2019-11-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 145 | 145 |  | µg/L | 6 | 24 | 2019-11-15
BC1119-4 | MORR WWTP | 2019-11-07 | 2019-11-07 | Total Nitrogen | SW | QC 10-107-04-4-B | 8167 | 8167 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-4 | MORR WWTP | 2019-11-07 | 2019-11-07 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 2337 | 2337 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-4 | MORR WWTP | 2019-11-07 | 2019-11-07 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 4346 | 4346 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-4 | MORR WWTP | 2019-11-07 | 2019-11-07 | Phosphorus, total | SW | QC 10-115-01-4-B | 206 | 206 |  | µg/L | 6 | 24 | 2019-11-15
BC1119-8 | JCSD/Mt. Evans Lab | 2019-11-08 | 2019-11-08 | Total Nitrogen | SW | QC 10-107-04-4-B | 38758 | 38758 |  | µg/L | 26 | 104 | 2019-11-15
BC1119-8 | JCSD/Mt. Evans Lab | 2019-11-08 | 2019-11-08 | Nitrate/Nitrite as N, dissolved | SW | QC 10-107-04-1-C | 36919 | 36919 |  | µg/L | 6 | 24 | 2019-11-08
BC1119-8 | JCSD/Mt. Evans Lab | 2019-11-08 | 2019-11-08 | Nitrogen, ammonia | SW | QC 10-107-06-2-A | 46 | 46 |  | µg/L | 10 | 40 | 2019-11-11
BC1119-8 | JCSD/Mt. Evans Lab | 2019-11-08 | 2019-11-08 | Phosphorus, total | SW | QC 10-115-01-4-B | 276 | 276 |  | µg/L | 6 | 24 | 2019-11-15